## GIS SS BOQ
Schedules of Rates and Prices
Package-I (LOT-1)
Schedule No. 1 - Plant and Mandatory Spare Parts Supplied from Abroad
Item | Description | Country of Origin | Unit | Qty. | Unit Price1 |  | Total Price1 | Taxes and Duties
[5 empty] | Foreign Currency | CIF or CIP | Foreign Currency | Local Currency
1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 = 5x 7 | 9
1 | Supply of132 KV GIS EQUIPMENTS
1.1 | Supply of 145kV, 2000 A, 40 kA for 3 sec, SF6 gas insulated Line feeder bay module each comprising of SF6 gas insulated circuit breaker, current transformer, bus-bar dis connectors with common grounding switch, dis connectors with safety grounding switch(es), high speed fault making grounding switch,local control cubicle, SF6 gas monitoring system for complete bay, gas insulated terminal connection for connecting Transformer (Oil/SF6 Bushing) with GIS through gas insulated interconnection bus etc to complete Transformer Bay Module. |  | SET | 2
1.2 | Supply of 145kV, 2000A, 40 kA for 3 sec , SF6 gas insulated Line feeder bay module each comprising of SF6 gas insulated circuit breaker, current transformer, bus-bar dis connectors with common grounding switch, dis connectors with safety grounding switch(es), high speed fault making grounding switch,local control cubicle, SF6 gas monitoring system for complete bay, gas insulated terminal connection for connecting overhead line (Air/SF6) with GIS through gas insulated interconnection bus etc.to complete Feeder Bay Module. |  | SET | 2
1.3 | Supply of 145kV , 40 kA for 3 sec, 3- phase Isolated , SF6 gas insulated , metal enclosed 3150A bus bars each enclosed in bus enclosures running along the length of the switchgear to interconnect each of circuit breaker bay module. Each bus bar set shall be complete with potential transformer, dis connectors , bus bar grounding switch, SF6 gas monitoring system for the complete bus etc. |  | SET | 2
1.4 | Supply of 145kV, 3150A, 40 kA for 3 sec, SF6 gas insulated Bus Coupler Bay Module comprising of SF6 gas insulated circuit breaker, current transformer, dis connectors switches, disconnector with safety grounding switch(es). Local control cubicle, SF6 gas monitoring system for the complete bay etc. |  | SET | 1
1.5 | Supply of 132 kV Power Cable XLPE insulated 800 Sqmm Copper for the GIS system connecting to Power Transformer and Bays |  | LOT | 1
1.6 | Supply of HV Test charges for 132 KV GIS |  | LOT | 1
2 | Supply of 33 KV GIS EQUIPMENT:
2.1 | Supply of 36 KV, 1250 A, 25 kA for 3 sec, SF6 gas insulated Line transfermor bay module each comprising of SF6 gas insulated circuit breaker, current transformer, bus-bar dis connectors with common grounding switch, dis connectors with safety grounding switch(es), high speed fault making grounding switch,local control cubicle, SF6 gas monitoring system for complete bay, gas insulated terminal connection for connecting Transformer (Oil/SF6 Bushing) with GIS through gas insulated interconnection bus etc to complete Transformer Bay Module. |  | SET | 2
2.2 | Supply of 36 KV, 1250A, 25 kA for 3 sec , SF6 gas insulated Line feeder bay module each comprising of SF6 gas insulated circuit breaker, current transformer, bus-bar dis connectors with common grounding switch, dis connectors with safety grounding switch(es), high speed fault making grounding switch,local control cubicle, SF6 gas monitoring system for complete bay, gas insulated terminal connection for connecting overhead line (Air/SF6) with GIS through gas insulated interconnection bus etc.to complete Feeder Bay Module. |  | SET | 5
2.3 | Supply of 36 KV, 1250A, 25 kA for 3 sec, SF6 gas insulated Bay Module comprising of SF6 gas insulated circuit breaker, current transformer, disconnectors switches, disconnector with safety grounding switch(es) & 36 KV , 25 kA for 3 sec, 3- phase Isolated , SF6 gas insulated , metal enclosed 2000 A bus bars each enclosed in bus enclosures running along the length of the switchgear to interconnect each of circuit breaker bay module. Each bus bar set shall be complete with potential transformer, dis conectors , bus bar grounding switch, Local control cubicle, SF6 gas monitoring system etc. |  | SET | 1
2.4 | Supply of 33 kV Power Cable XLPE insulated 630 Sqmm Copper for the GIS system connecting to Power Transformer and 33 kV Bays |  | LOT | 1
3 | Supply of SUBSTATION EARTHING SYSTEMS ( As Per Technical Specification) |  | LOT | 1
4 | Supply of POWER CABLES,1.1KV,XLPE & PVC ,ARMOURED, ALUMINIUM CONDUCTOR (As per Technical Specification) |  | LOT | 1
5 | Supply of CONTROL CABLES 1.1 kV PVC Stranded COPPER As per technical specification |  | LOT | 1
6 | Supply of ACCESSORIES FOR OPGW SYSTEM ( AS PER TECHNICAL SPECIFICATION) |  | LOT | 3
7 | Supply of EPABX(Telephone Exchange) standard complied to ITU-T-G-711,G-712,Q-507, Q-517 capacity 16 lines /Trunks (2W,4W,RSU),Universal Numbering scheme,Operating console,Desktop PC-Menue driven. |  | No | 1
8 | SUPPLY OF STATION TRANSFORMER 33KV/433V,250 KVA & OTHER MATERIALS FOR MEETING THE AUXILIARY SUPPLY OF THE SUB-STATION AS PER TECHNICAL SPECIFICATION |  | No | 2
9 | Supply of SUB-STATION SWITCH YARD LIGHTING,IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED) of reputed make (Philips/CGL/Bajaj) with switch gear,GI Conduit etc.(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be maintained). |  | LOT | 1
10 | Supply of PROTECTION,CONTROL METERING, EVENT LOGGER,BUS BAR PROTN PAN AS PER TECH SPEC WITH SUB-STATION AUTOMATION(132kV side) IEC 61850 compliant & as per technical specification. |  | SET | 1
11 | 132 KV SIDE Supply of SUB-STATION AUTOMATION SYSTEM (COMPRISING OF 02 Nos. FEEDER BAYS + 02 TRANSFORMER BAYS + 01 Nos. BUS COUPLER BAYS) |  | SET | 1
11.1 | Supply of BCU FOR CONTROLLING AND MONITORING OF AUXILIARY SYSTEM & OTHER ACCESSORIES( COMPRISING SERVERS,ENGG STATION,WORKS STATION,UPS etc (TO BE LOCATED IN THE CENTRAL CONTROL ROOM)FOR BOTH 220 & 33 KV SIDE OF THE GIS SUB-STATION. As per Technical specification. |  | SET | 1
11.2 | Supply of FEEDER PROTECTION RELAY PANEL(MAIN-I & MAIN-II PROTECTION WITH AUTO RECLOSURE ) |  | NOS | 2
11.3 | Supply of TRANSFORMER PROTECTION RELAY PANEL (MAIN-I & MAIN-II PROTECTION CONSIDERING BOTH HV & LV) |  | NOS | 2
11.4 | Supply of BUS COUPLER PROTECTION RELAY PANEL |  | NOS | 1
11.5 | Supply of BUS-BAR(DUPLICATED) PROTECTION RELAY PANEL |  | SET | 1
12 | 33 KV SIDE Supply of FEEDER PROTECTION RELAY PANEL |  | NOS | 5
12.1 | Supply of TRANSFORMER PROTECTION RELAY PANEL132/33 KV, 40 MVA) |  | NOS | 2
12.2 | Supply of TRANSFORMER PROTECTION RELAY PANEL(2X 33/0.43 KV, 250 KVA) |  | NOS | 1
13 | Supply of AC SYSTEM: MAIN AC DB,(HAVING 800 A,50KA,DRAWOUT TYPE ACB WITH 3 O/C,E/F,U/V RELAYING FACILITY INDOOR TYPE AS PER SPECIFICATION.(MAIN DB-1,MAIN DB-2 WITH B/C), ACDB,MAIN LIGHTING DISTRIBUTION BOARD, INDOOR LIGHTING DISTRIBUTION BOARD, EMERGENCY LIGHTING DISTRIBUTION BOARD & INDOOR RECEPTACLE BOARD etc. |  | SET | 1
14 | Supply of DC SYSTEM: 220 V DC BOARD (HAVING 100A DC MCCB AS INCOMER, E/F (EARTH LEAKAGE), UNDER & OVER VOLTAGE AS PER SPECIFICATION (DC DB-1,DC DB-2 & B/C), 220 V DC EMERGENCY DISTRIBUTION BOARD, BATTERY CHARGER, DISTILLED WATER PLANT, OTHER TOOLS AND PLANTS (T&P's) |  | SET | 1
15 | Supply of materials for 33 kV Out going feeders (AIS) 5(five) Nos
15.1 | Supply of 33kV LA |  | Nos | 15
15.2 | Supply of 33kV cable termination kit for AIS bushing |  | Nos | 5
15.3 | Supply of materials for 33kV AIS Structure with Civil foundation |  | Lot | 5
16 | Supply of OFFICE FURNITURE as per requirement (Godrej make) |  | LOT | 1
17 | Supply of EOT Crane for 132 kV GIS Hall (5T Capacity) including all accessories with control panel.) |  | No | 1
18 | 132/33 kV, 40 MVA Transformer (No) ( Supplied by OWNER) |  | No | 2
18.1 | Supply of materials for Foundation of Power Transformer as per Tech. Specification |  | No | 2
19 | Supply of materials for GIS Sub Station Building , Control room and Foundation ( As per specified layout drawings) |  | No | 1
20 | Supply of materials for Sub Station Civil work
20.1 | Supply of materials for Boundary Wall with main GI gate as per specification |  | Mtr | 985
20.2 | Supply of materials for Sub station earth filling |  | Cum | 6675
20.3 | Supply of materials for Sub station campus road as per specification |  | Mtr | 350
20.4 | Supply of materials for Sub station drainage as per specification |  | Mtr | 400
21 | Supply of materials for Water system like 4 inch Dia bore well with Quality Pipes, 0.5 HP submersivele pump, 1000 lts OH tank, Sanitary fittings,switch yard water hydrant system, tap for garden etc |  | LOT | 1
22 | SUPPLY OF ESSENTIAL TOOLS
22.1 | Enclosure insulators and main circuit of bus bar |  | Set | 1
22.2 | SF6 Pressure gauges |  | Set | 2
22.3 | SF6 Pressure relief devices |  | Set | 2
22.4 | Oil pressure switch |  | Set | 2
22.5 | SF6 gas in steel bottle 52 Kg / bottle |  | Nos. | 2
22.6 | Hydraulic Pump/spring charge motor for circuit breakers |  | Set | 1
22.7 | Rupture disc for circuit breakers / potential transformer |  | Nos. | 1
22.8 | Rupture disc for other compartments |  | Nos. | 2
22.9 | SF6 gas leak detector |  | Set | 1
22.1 | Hygrometer |  | Set | 1
22.11 | Milli volt drop measurement appliance |  | Set | 1
22.12 | One set of pipe grooving tools for the hydraulic operating mechanism |  | Set | 1
TOTAL Column 8 to be carried forward to Schedule No. 5. Grand Summary
Name of Bidder
Signature of Bidder
Country of Origin Declaration Form
Item | Description |  |  |  |  | Country
Schedules of Rates and Prices
Package-I (LOT-1)
Schedule No. 2 - Plant and Mandatory Spare Parts Supplied from Within the Employer’s Country
Item | Description | Unit | Qty | EXW Unit Price1 | Total EXW Price1 | Sales Tax | Total Sales Tax | Entry | Total Entry Tax | Total Price
[6 empty] | (CST/VAT) | (CST/VAT) | Tax
1 | 2 | 3 | 4 | 5 | 6=3X5 | 7 | 8=4X7 | 9 | 10=4X9 | 11=6+8+10
1 | Supply of 132 KV GIS EQUIPMENTS
1.1 | Supply of 145kV, 2000 A, 40 kA for 3 sec, SF6 gas insulated Line feeder bay module each comprising of SF6 gas insulated circuit breaker, current transformer, bus-bar, disconnectors with common grounding switch, dis connectors with safety grounding switch(es), high speed fault making grounding switch,local control cubicle, SF6 gas monitoring system for complete bay, gas insulated terminal connection for connecting Transformer (Oil/SF6 Bushing) with GIS through gas insulated interconnection bus etc to complete Transformer Bay Module. | SET | 2
1.2 | Supply of 145kV, 2000A, 40 kA for 3 sec , SF6 gas insulated Line feeder bay module each comprising of SF6 gas insulated circuit breaker, current transformer, bus-bar disconnectors with common grounding switch, dis connectors with safety grounding switch(es), high speed fault making grounding switch,local control cubicle, SF6 gas monitoring system for complete bay, gas insulated terminal connection for connecting overhead line (Air/SF6) with GIS through gas insulated interconnection bus etc.to complete Feeder Bay Module. | SET | 2
1.3 | Supply of 145kV , 40 kA for 3 sec, 3- phase Isolated , SF6 gas insulated , metal enclosed 3150A bus bars each enclosed in bus enclosures running along the length of the switchgear to interconnect each of circuit breaker bay module. Each bus bar set shall be complete with potential transformer, dis connectors , bus bar grounding switch, SF6 gas monitoring system for the complete bus etc. | SET | 2
1.4 | Supply of 145kV, 3150A, 40 kA for 3 sec, SF6 gas insulated Bus Coupler Bay Module comprising of SF6 gas insulated circuit breaker, current transformer, dis connectors switches, disconnector with safety grounding switch(es). Local control cubicle, SF6 gas monitoring system for the complete bay etc. | SET | 1
1.5 | Supply of 132 kV Power Cable XLPE insulated 800 Sqmm Copper for the GIS system connecting to Power Transformer and Bays | LOT | 1
1.6 | Supply of HV Test charges for 132 KV GIS | LOT | 1
2 | Supply of 33 KV GIS EQUIPMENT:
2.1 | Supply of 36 KV, 1250 A, 25 kA for 3 sec, SF6 gas insulated Line transfermor bay module each comprising of SF6 gas insulated circuit breaker, current transformer, bus-bar dis connectors with common grounding switch, dis connectors with safety grounding switch(es), high speed fault making grounding switch,local control cubicle, SF6 gas monitoring system for complete bay, gas insulated terminal connection for connecting Transformer (Oil/SF6 Bushing) with GIS through gas insulated interconnection bus etc to complete Transformer Bay Module. | SET | 2
2.2 | Supply of 36 KV, 1250A, 25 kA for 3 sec , SF6 gas insulated Line feeder bay module each comprising of SF6 gas insulated circuit breaker, current transformer, bus-bar dis connectors with common grounding switch, dis connectors with safety grounding switch(es), high speed fault making grounding switch,local control cubicle, SF6 gas monitoring system for complete bay, gas insulated terminal connection for connecting overhead line (Air/SF6) with GIS through gas insulated interconnection bus etc.to complete Feeder Bay Module. | SET | 5
2.3 | Supply of 36 KV, 1250A, 25 kA for 3 sec, SF6 gas insulated Bus Coupler Bay Module comprising of SF6 gas insulated circuit breaker, current transformer, disconnectors switches, disconnector with safety grounding switch(es) & 36 KV , 25 kA for 3 sec, 3- phase Isolated , SF6 gas insulated , metal enclosed 2000 A bus bars each enclosed in bus enclosures running along the length of the switchgear to interconnect each of circuit breaker bay module. Each bus bar set shall be complete with potential transformer, dis conectors , bus bar grounding switch, Local control cubicle, SF6 gas monitoring system etc. | SET | 1
2.4 | Supply of 33 kV Power Cable XLPE insulated 630Sqmm Copper for the GIS system connecting to Power Transformer and 33 kV Bays | LOT | 1
4 | Supply of SUBSTATION EARTHING SYSTEMS As per Technical specification | LOT | 1
5 | Supply of POWER CABLES,1.1KV,XLPE & PVC ,ARMOURED, ALUMINIUM CONDUCTOR (As per Technical Specification) | LOT | 1
6 | Supply of CONTROL CABLES 1.1 kV PVC Stranded COPPER As per technical specification | LOT | 1
6 | Supply of ACCESSORIES FOR PLLC/OPGW SYSTEM AS PER TECHNICAL SPECIFICATION) | LOT | 3
7 | Supply of EPABX(Telephone Exchange) standard complied to ITU-T-G-711,G-712,Q-507, Q-517 capacity 16 lines /Trunks (2W,4W,RSU),Universal Numbering scheme,Operating console,Desktop PC-Menue driven. | No | 1
8 | SUPPLY OF STATION TRANSFORMER 33KV/0.433 kV,250 KVA & OTHER MATERIALS FOR MEETING THE AUXILIARY SUPPLY OF THE SUB-STATION AS PER TECHNICAL SPECIFICATION | No | 2
9 | Supply of SUB-STATION SWITCH YARD LIGHTING,IT INCLUDES SUPPLY OF FIXTURES & LAMPS (LED) of reputed make (Philips/CGL/Bajaj) with switch gear,GI Conduit etc.(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be maintained). | LOT | 1
10 | Supply of PROTECTION,CONTROL METERING, EVENT LOGGER,BUS BAR PROTN PAN AS PER TECH SPEC WITH SUB-STATION AUTOMATION(132kV side) IEC 61850 compliant & as per technical specification. | SET | 1
11 | 132 KV SIDE Supply of SUB-STATION AUTOMATION SYSTEM (COMPRISING OF 02 Nos. FEEDER BAYS + 02 TRANSFORMER BAYS + 01 Nos. BUS COUPLER BAYS) | SET | 1
11.1 | Supply of BCU FOR CONTROLLING AND MONITORING OF AUXILIARY SYSTEM & OTHER ACCESSORIES( COMPRISING SERVERS,ENGG STATION,WORKS STATION,UPS etc (TO BE LOCATED IN THE CENTRAL CONTROL ROOM)FOR BOTH 220 & 33 KV SIDE OF THE GIS SUB-STATION. As per Technical specification. | SET | 1
11.2 | Supply of FEEDER PROTECTION RELAY PANEL(MAIN-I & MAIN-II PROTECTION WITH AUTO RECLOSURE ) | NOS | 2
11.3 | Supply of TRANSFORMER PROTECTION RELAY PANEL (MAIN-I & MAIN-II PROTECTION CONSIDERING BOTH HV & LV) | NOS | 2
11.4 | Supply of BUS COUPLER PROTECTION RELAY PANEL | NOS | 1
11.5 | Supply of BUS-BAR(DUPLICATED) PROTECTION RELAY PANEL | SET | 1
12 | 33 KV SIDE Supply of FEEDER PROTECTION RELAY PANEL | NOS | 5
12.1 | Supply of TRANSFORMER PROTECTION RELAY PANEL132/33 KV, 40 MVA) | NOS | 2
12.2 | Supply of TRANSFORMER PROTECTION RELAY PANEL(2X 33/0.43 KV, 250 KVA) | NOS | 1
13 | Supply of AC SYSTEM: MAIN AC DB,(HAVING 800 A,50KA,DRAWOUT TYPE ACB WITH 3 O/C,E/F,U/V RELAYING FACILITY INDOOR TYPE AS PER SPECIFICATION.(MAIN DB-1,MAIN DB-2 WITH B/C), ACDB,MAIN LIGHTING DISTRIBUTION BOARD, INDOOR LIGHTING DISTRIBUTION BOARD, EMERGENCY LIGHTING DISTRIBUTION BOARD & INDOOR RECEPTACLE BOARD etc. | SET | 1
14 | Supply of DC SYSTEM: 220 V DC BOARD (HAVING 100A DC MCCB AS INCOMER, E/F (EARTH LEAKAGE), UNDER & OVER VOLTAGE AS PER SPECIFICATION (DC DB-1,DC DB-2 & B/C), 220 V DC EMERGENCY DISTRIBUTION BOARD, BATTERY CHARGER, DISTILLED WATER PLANT, OTHER TOOLS AND PLANTS (T&P's) | SET | 1
15 | Supply of materials for 33 kV Out going feeders (AIS) 5(five) Nos
15.1 | 33kV LA | Nos | 16
15.2 | 33kV cable termination kit for AIS bushing | Nos | 5
15.3 | 33kV GIS Structure with Civil foundation | LS
16 | Supply of OFFICE FURNITURE as per requirement (Godrej make) | LOT | 1
17 | Supply of EOT Crane for 132 kV GIS Hall (5T Capacity) including all accessories with control panel. | No | 1
18 | 132/33 kV, 40 MVA Transformer ( Supplied by OWNER) | Nos | 2
18.1 | Supply of materials for Foundation of Power Transformer as per Tech. Specification | No | 2
19 | Supply of materials for GIS Sub Station Building , Control room and Foundation ( As per specified layout drawings) | No | 1
20 | Supply of materials for Sub Station Civil work
20.1 | Supply of materials for Boundary Wall with main GI gate as per specification | Mtr | 985
20.2 | Supply of materials for Sub station earth filling | Cum | 6675
20.3 | Supply of materials for Sub station campus road as per specification | Mtr | 350
20.4 | Supply of materials for Sub station drainage as per specification | Mtr | 400
21 | Supply of materials for Water system like 4 inch Dia bore well with Quality Pipes, 0.5 HP submersivele pump, 1000 lts OH tank, Sanitary fittings,switch yard water hydrant system, tap for garden etc | LOT | 1
22 | SUPPLY OF ESSENTIAL TOOLS
22.1 | Enclosure insulators and main circuit of bus bar | Set | 1
22.2 | SF6 Pressure gauges | Set | 2
22.3 | SF6 Pressure relief devices | Set | 2
22.4 | Oil pressure switch | Set | 2
22.5 | SF6 gas in steel bottle 52 Kg / bottle | Nos. | 2
22.6 | Hydraulic Pump/spring charge motor for circuit breakers | Set | 1
22.7 | Rupture disc for circuit breakers / potential transformer | Nos. | 1
22.8 | Rupture disc for other compartments | Nos. | 2
22.9 | SF6 gas leak detector | Set | 1
22.1 | Hygrometer | Set | 1
22.11 | Milli volt drop measurement appliance | Set | 1
22.12 | One set of pipe grooving tools for the hydraulic operating mechanism | Set | 1
TOTAL Column 6 to be carried forward to Schedule No. 5. Grand Summary
Name of Bidder
Signature of Bidder
Schedules of Rates and Prices
Package-I (LOT-1)
Schedule No. 4 - Installation and Other Services
Item | Description | Unit | Qty. | Unit Price1 |  | Total Price1 |  | Unit Service Tax | Total Service Tax
|  |  |  | Local Currency Portion | Foreign Currency Portion | Local Currency Portion | Foreign Currency Portion | Local Currency Portion | Local Currency Portion
1 | 2 | 3 | 4 | 5 | 6 | 7=4X5 | 8=4x6 | 9 | 10
1 | Transportation, Storing ,Erection, Testing & Commissioning and Other Services of 145KV GIS EQUIPMENTS including Civil Works | SET
1.1 | Transportation, Storing, Erection , Testing & Commissioning of 145kV, 2000 A, 40 kA for 3 sec, SF6 gas insulated Line feeder bay module each comprising of all equipments to complete Transformer Bay Module. | SET | 2
1.2 | Transportation, Storing, Erection , Testing & Commissioning of 145kV, 2000A, 40 kA for 3 sec , SF6 gas insulated Line feeder bay module each comprising of all equipments to complete Feeder Bay Module. | SET | 2
1.3 | Transportation, Storing, Erection , Testing & Commissioning of 145kV , 40 kA for 3 sec, 3- phase Isolated , SF6 gas insulated , metal enclosed 3150A bus bars each enclosed in bus enclosures running along the length of the switchgear to interconnect each of circuit breaker bay module with SF6 gas monitoring system for the complete bus etc. | SET | 2
1.4 | Transportation, Storing, Erection , Testing & Commissioning of 145kV, 3150A, 40 kA for 3 sec, SF6 gas insulated Bus Coupler Bay Module comprising of SF6 gas insulated circuit breaker with Local control cubicle, SF6 gas monitoring system for the complete bay etc. | LOT | 1
1.5 | Transportation, Storing, Erection , Testing & Commissioning of HV Test charges for 132 KV GIS | LOT | 1
2 | Transportation, Storing, Erection , Testing & Commissioning of Other Services of 33 KV GIS EQUIPMENTS including Civil Works
2.1 | Transportation, Storing, Erection , Testing & Commissioning of 36 KV, 1250 A, 25 kA for 3 sec, SF6 gas insulated Line transfermor bay module each comprising of all equipments to complete Transformer Bay Module. | SET | 2
2.2 | Transportation, Storing, Erection , Testing & Commissioning of 36 KV, 1250A, 25 kA for 3 sec , SF6 gas insulated Line feeder bay module each comprising of all equipment to complete Feeder Bay Module. | SET | 5
2.3 | Transportation, Storing, Erection , Testing & Commissioning of 36 KV, 1250A, 25 kA for 3 sec, SF6 gas insulated Bus Coupler Bay Module comprising of all equipments with SF6 gas monitoring system etc. | SET | 1
2.4 | Transportation, Storing, Erection , Testing & Commissioning of XLPE Power Copper conductor cable for the GIS system (132 & 33 KV class). 132KV XLPE CABLE 800 sq mm & 33KV CABLE 630 SQ. MM | LOT | 1
3 | Transportation, Storing, Erection , Testing & Commissioning of SUBSTATION EARTHING SYSTEMS | LOT | 1
4 | Transportation, Storing, Laying , Testing and Commissioning of POWER CABLES, ALUMINIUM CONDUCTOR (As per Specification) | LOT | 1
5 | Transportation , Storing, laying , Testing and Commissioning of CONTROL CABLES 1.1 kV PVC Stranded COPPER As per technical specification | LOT | 1
6 | Transportation , Storing,Erection, Testing and Commissioning of PLLC/OPGW SYSTEM AS PER TECHNICAL SPECIFICATION) | LOT | 3
7 | Transportation , Storing,Erection, Testing and Commissioning of EPABX(Telephone Exchange) standard complied to ITU-T-G-711,G-712,Q-507, Q-517 capacity 16 lines /Trunks (2W,4W,RSU),Universal Numbering scheme,Operating console,Desktop PC-Menue driven. | No | 1
8 | Transportation , Storing,Erection , Testing and Commissioning of STATION TRANSFORMER 33KV/0.433kV,205 KVA & OTHER MATERIALS FOR MEETING THE AUXILIARY SUPPLY OF THE SUB-STATION including Civil foundation works | No | 2
9 | Transportation , Storing, Erection, Testing and Commissioning of SUB-STATION SWITCH YARD LIGHTING,(Lighting fixtures are to be fixed rigidly on the Column at a suitable height so that the required lux can be maintained). | LOT | 1
10 | Transportation , Storing,Erection , Testing and Commissioning of PROTECTION CONTROL & METERING, EVENT LOGGER,BUS BAR PROTN PAN AS PER TECH SPEC WITH SUB-STATION AUTOMATION(132kV side) IEC 61850 compliant & as per technical specification. | SET | 1
11 | 132 KV SIDE Transportation , Storing, Erection, Testing and Commissioning of SUB-STATION AUTOMATION SYSTEM (COMPRISING OF 02 Nos. FEEDER BAYS + 02 TRANSFORMER BAYS + 01 Nos. BUS COUPLER BAYS) | SET | 1
11.1 | Transportation , Storing, Erection, Testing and Commissioning of BCU FOR CONTROLLING AND MONITORING OF AUXILIARY SYSTEM & OTHER ACCESSORIES( COMPRISING SERVERS,ENGG STATION,WORKS STATION,UPS etc (TO BE LOCATED IN THE CENTRAL CONTROL ROOM)FOR BOTH 220 & 33 KV SIDE OF THE GIS SUB-STATION. As per Technical specification. | SET | 1
11.2 | Transportation , Storing, Erection, Testing and Commissioning of FEEDER PROTECTION RELAY PANEL(MAIN-I & MAIN-II PROTECTION WITH AUTO RECLOSURE ) | NOS | 2
11.3 | Transportation , Storing, Erection, Testing and Commissioning of TRANSFORMER PROTECTION RELAY PANEL (MAIN-I & MAIN-II PROTECTION CONSIDERING BOTH HV & LV) | NOS | 2
11.4 | Transportation , Storing, Erection, Testing and Commissioning of BUS COUPLER PROTECTION RELAY PANEL | NOS | 1
11.5 | Transportation , Storing, Erection, Testing and Commissioning of BUS-BAR(DUPLICATED) PROTECTION RELAY PANEL | SET | 1
12 | 33 KV SIDE Transportation , Storing, Erection, Testing and Commissioning of FEEDER PROTECTION RELAY PANEL | NOS | 5
12.1 | Transportation , Storing, Erection, Testing and Commissioning of TRANSFORMER PROTECTION RELAY PANEL132/33 KV, 40 MVA) | NOS | 2
12.2 | Transportation , Storing, Erection, Testing and Commissioning of TRANSFORMER PROTECTION RELAY PANEL(2X 33/0.43 KV, 250 KVA) | NOS | 1
13 | Transportation, Storing, Erection, Testing and Commissioning of AC SYSTEM: MAIN AC DB,(HAVING 800 A,50KA,DRAWOUT TYPE ACB WITH 3 O/C,E/F,U/V RELAYING FACILITY INDOOR TYPE AS PER SPECIFICATION.(MAIN DB-1,MAIN DB-2 WITH B/C), ACDB,MAIN LIGHTING DISTRIBUTION BOARD, INDOOR LIGHTING DISTRIBUTION BOARD, EMERGENCY LIGHTING DISTRIBUTION BOARD & INDOOR RECEPTACLE BOARD etc. | SET | 1
14 | Transportation, Storing, Erection, Testing and Commissioning of DC SYSTEM: 220 V DC BOARD (HAVING 100A DC MCCB AS INCOMER, E/F (EARTH LEAKAGE), UNDER & OVER VOLTAGE AS PER SPECIFICATION (DC DB-1,DC DB-2 & B/C), 220 V DC EMERGENCY DISTRIBUTION BOARD, BATTERY CHARGER, DISTILLED WATER PLANT, OTHER TOOLS AND PLANTS (T&P's) | SET | 1
15 | Transporting, Storing, Erection, & Commissioning of materials for 33 kV Out going feeders (AIS) 5 (five) Nos
15.1 | 33kV LA | Nos | 15
15.2 | 33kV cable termination kit for AIS bushing | Nos | 5
15.3 | 33kV GIS Structure with Civil foundation | LS
16 | Transporting, Storing, Erection, & Commissioning of EOT Crane for 132 kV GIS Hall (5T Capacity) including all accessories with control panel. | No | 1
17 | Transporting ,Storing ,Erection, Testing & Commissioning of 132/33 kV, 40 MVA Transformer including Transformer other works As per Technical Specification | No | 2
18 | Transporting ,Storing ,construction of Foundation of Power Transformer with waste oil pit as per Tech. Specification | No | 2
19 | Transporting, Storeing , Constructing & Commissioning of Sub Station GIS Building for 132kV and 33 kV with EHV Cable Basement , Controlroom and other arrangements as Specified in the Drawing | LOT | 1
20 | Transporting ,Storing ,Erection, Testing & Commissioning ofmaterials for Sub Station Civil work
20.1 | Transporting ,Storing ,construction of Boundary Wall with main GI gate as per specification | Mtr | 985
20.2 | Transporting ,Storing ,Filling of Sub station with barrowedv earth | Cum | 6675
20.3 | Transporting ,Storing ,construction of Sub station campus road as per specification | Mtr | 350
20.4 | Transporting ,Storing ,construction of Sub station drainage as per specification | Mtr | 400
20.5 | Transporting, Storing, Drilling & Commissioning of Water system like 4 inch Dia bore well with Quality Pipes,1.0 HP submersivele pump, 2000 lts OH tank, Sanitary fittings,switch yard water hydrant system, tap for garden etc | LOT | 1
TOTAL Columns 7 and 8 tobe carried forward to Schedule No. 5. Grand Summary
Name of Bidder
Signature of Bidder
Schedules of Rates and Prices
Package-I (LOT-1)
Schedule No. 5 - Grand Summary
Schedule No. | Title | Total 1
|  | Foreign | Local
1 | Plant and Mandatory Spare Parts Supplied from Abroad
2 | Plant and Mandatory Spare Parts Supplied from Within the Employer’s Country
3 | Design Services
4 | Installation and Other Services
GRAND TOTAL to be carried forward to Letter of Bid
Name of Bidder
Signature of Bidder