# LT Aerial Bunched Cables for LT Lines

# (APPLICABLE FOR LT AB CABLE WITH XLPE INSULATION ONLY)

- SCOPE:

This specification covers XLPE insulated Aluminum cable twisted over a central bare Aluminum Alloy messenger wire for use of L.T. Over-Headlines in Rural Electrification System. The Aerial Bunched cable and messenger wire should be confirming to IS.

(Sizes: of the cable)

| 1.01 | 1X16 (Ph) + 1X25 (bare messenger cum neutral) SQ. MM. |
| --- | --- |
| 1.02 | 1X16 (Ph) + 1X25 (bare messenger cum neutral) + 1x16 (insulated Street lighting)SQ. MM. |
| 1.03 | 3X16(Ph)+1X25 (bare messenger cum neutral) SQ. MM. |
| 1.04 | 3 X 16(Ph) +1x25 (bare messenger cum neutral) + 1x16 (insulated Street lighting) SQ. MM. |
| 1.05 | 1X25(Ph)+1x25 (bare messenger cum neutral) SQ. MM. |
| 1.06 | 1X25(Ph) + 1X25 (bare messenger cum neutral) + 1x16 (insulated Street lighting) SQ. MM. |
| 1.07 | 3X25(Ph)+1X25 (bare messenger cum neutral) SQ. MM. |
| 1.08 | 3 X 25(Ph) +1x25 (bare messenger cum neutral) + 1x16 (insulated Street lighting) SQ. MM. |
| 1.09 | 1X35(Ph)+1X25 (bare messenger cum neutral) SQ. MM. |
| 1.10 | 1x35(Ph) + 1X25 (bare messenger cum neutral) + 1x16 (insulated Street lighting) SQ. MM. |
| 1.11 | 3X35(Ph)+1X25 (bare messenger cum neutral) SQ. MM. |
| 1.12 | 3X35 (Ph) + 1x25 (bare messenger cum neutral)+ 1x16 (insulated Street lighting) SQ. MM. |
| 1.13 | 3X50(Ph)+1X35 (bare messenger cum neutral) SQ. MM. |
| 1.14 | 3X50 (Ph)+1x35 (bare messenger cum neutral) +1x16 (insulated Street lighting) SQ. MM. |
| 1.15 | 3X95(Ph)+1X70 (bare messenger cum neutral) SQ. MM. |

1.16    3X95(Ph)+1X70 (bare messenger cum neutral) SQ. MM+1x16 (insulated Street lighting) SQ. MM

- RATED VOLTAGE:

The rated voltage of the AB cables shall be 1100 volts

- APPLICABLE STANDARDS:

Unless otherwise stipulated in this specification the following Standards shall be applicable.

- IS – 14255/1995   :  ABC cables 1100 volts.

- IS – 8130/1984 : Conductors for insulated cables.

- IS – 398/Pt.IV/1994: Aluminium alloy conductor.

- IS – 10418/1982   : Drums for electric cables

- GENERAL:

The AB cable covered under this specification should be suitable for use on three phase, 4 wire earthed system for working voltage up to 1100 V. It should confirm the relevant standards stated above and others if applicable.

The phase conductor shall be 95 mm², 50 mm², 35 mm, 25 mm² and 16 mm²  XLPE insulated and the messenger-cum-neutral conductor of sizes 70 mm², 35 mm² and 25 mm² shall be bare heat treated aluminium-magnesium-silicon alloy wires containing 0.5% magnesium and approximately 0.5% silicon confirming to IS: 398 (Part-IV):1979 and its latest amendment, if any.

- PHASE CONDUCTORS:

  - The phase & street lighting conductor shall be provided cross linked poly ethylene insulation applied by extrusion. The thickness of insulation shall not be less than 1.2 mm up to 35mm² and shall not be less than 1.5 mm for above 35mm² at any point and insulation shall be so applied that it fits closely on the conductor and it shall be possible to remove it without damaging the conductor. The insulated conductors shall generally conform to the standards IS-14255:1995.

  - The phase conductors shall be provided with one, two & three ‘ridges’ for easy identification.

  - The tensile strength of the aluminum wire used in the conductor shall not be less 90 N/mn².

  - The standard size and technical characteristics of the phase conductors shall be as shown in the Table-1.

TABLE-I

| Nominal Sectional area in mm² | No. of Strands (IS 8130 –Table 2) | Dia. of Compacted conductor in mm (IS 10462 Pt 1 –Table 1) | Approx. Mass Kg/KMs. | Max. DC Résistance at 20ºc (Ohm/km) | Insulation Thickness in mm (IS 14255-Table 2) |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 |  |
| 16 | 7 | 4.4 | 42 | 1.91 | 1.2 |  |
| 25 | 7 | 5.5 | 65 | 1.20 | 1.2 |  |
| 35 | 7 | 6.8 | 95 | 0.868 | 1.2 |  |
| 50 | 7 | 7.9 | 127 | 0.641 | 1.5 |  |
| 70 | 19 | 9.4 | 184 | 0.443 | 1.5 |  |
| 95 | 19 | 11.0 | 254 | 0.320 | 1.5 |  |

MESSENGER-CUM-NEUTRAL WIRE:

- The bare messenger wire shall be of aluminium alloy generally confirming to IS–398/Pt.IV/94 composed of 7 strands and shall be suitable compacted or stranded to have smooth round surface to avoid damages to the overall insulation of phase & neutral conductor twisted around the messenger.

- There shall be no joint in any wire of the stranded messenger Conductor except these made in the base rod or wires before final drawing.

- The sizes and other technical characteristics of the messenger wire shall be as given in the Table No.2.

TABLE –2

| Nominal Sectional Area in mm² | No. of strands | Diameter of Compacted conductor in mm | Diameter of Stranded conductor in mm (Table 3 IS-10462 Pt 1) | Approx. Mass Kgs/KMs | Max .DC Resistance At 20 deg C (Ohm/km) |
| --- | --- | --- | --- | --- | --- |
| 1 | 2 | 3 | 4 | 5 | 6 |
| 25 | 7 | 5.8 | 6.42 | 65 | 1.380 |
| 35 | 7 | 6.8 | 7.56 | 95 | 0.986 |
| 70 | 7 | 9.44 | 10.65 | 185 | 0.492 |

NOTE: while limiting values in col. 3 is to be guaranteed a tolerance of + 10 % will be permissible

- XLPE INSULATION:

The insulation shall generally confirm to IS-14255

| Sr.No. | Property | Requirement |  |
| --- | --- | --- | --- |
| 1 | Tensile Strength | 12.5 N / mm² Min |  |
| 2 | Elongation at break | 200 % Min. |  |
| 3 | Ageing in air over |  |  |
| a | Treatment: Temperature & duration | 135 ± 3ºC & 7 days |  |
| b | Tensile strength variation | ± 25% Max. |  |
| c | Elongation variation | ± 25% Max. |  |
| 4 | Hot Set |  |  |
|  | Treatment temperature, | 200 ± 3ºC, |  |
| a | Time | 15 minutes |  |
|  | Under load, mechanical stresses | 20 N /cm². |  |
| b | Elongation under load | 175 % max. |  |
| c | Permanent elongation (set) after cooling | 15 % Max |  |
| 5 | Shrinkage |  |  |
| a | Treatment temperature duration | 130 ± 3ºC |  |
|  |  | For 1 hour |  |
| b | Shrinkage | 4% Max |  |
| 6 | Water absorption (Gravimetric) |  |  |
| a | Treatment– Temp. | 85 ± 2ºC |  |
|  | Duration | 14 days |  |
| b | Water absorbed | 1 mg. / cm² max. |  |

- TYPE TEST:

- Test for Phase/Street Light Conductors

- Tensile Test (IS-8130)

- Wrapping Test (IS-8130)

- Conductor Resistance Test (IS-8130)

- Test for Messenger:

- Breaking load test (to be made on finished conductor) -(IS-398/ Pt.IV/ 1994 with latest revision)

- Elongation test (IS - 398 / Pt.IV/1994)

- Resistance test (IS - 398 / Pt. IV /1994)

- If insulated , the test of insulation as per relevant IS will be applicable

- Physical test for XLPE insulation

- Tensile strength and Elongation at break

- Ageing in air oven

- Hot set test

- Shrinkage test

- Water absorption (Gravimetric)

- Carbon black 1. Content & 2. Dispersion

- Test for thickness of insulation

- Insulation Resistance (Volume Resistivity ) Test

- High Voltage Test

Note: The Manufacturer should submit the entire above type test of Govt. of India’s approved Laboratory along with their offer.

Optional Test:

Bending test on the completed cable:

Bending test shall be performed on a sample of complete cable. The sample shall be bent around a test mandrel at room temperature for at least one complete turn. It shall then be unwound and the process shall be repeated after turning the sample around its axis 1800. The cycle of this operation shall be then repeated twice.

The diameter of mandrel shall be 10 (D+d).

Where

D = Actual diameter of cable (i.e. the min. circumscribing diameter in mm) d = Actual diameter of the phase conductor in mm

No cracks visible to the naked eye are allowed.

- ACCEPTANCE TESTS:

Tests for Phase / Street Light Conductors:

- Tensile test (for Phase / Street light conductor)

- Wrapping test (for Phase / Street light conductor)

- Breaking load test for messenger conductor

- Elongation  test for messenger conductor

- Conductor Resistance test

- Test for thickness of insulation

- Tensile strength and elongation at break test

- Hot set test ( For XLPE insulation)

- Insulation Resistance test

- High voltage test

- PACKING MARKING:

- The LT AB cable shall be wound in nonreturnable drums conforming to IS-10418/1982 “Specification for Reels and Drums for bare wire” of the latest version thereof. The drums shall be marked with the following:

- Manufacturers name

- Trade mark if any

- Drum number

- Size of Conductor

- Size of Messenger

- Voltage grade

- Number of lengths of pieces of Cable in each drum

- Gross mass of the packing

- Net mass of Cable

- ISI mark

- The drums shall be of such a construction as to assure delivery of conductor in field free from displacement and damage and should be able to withstand all stresses due to handling and the stringing operation so that cable surface not dented, scratched or damaged in any way during transport and erection. The cable shall be properly lugged on the drums

- The cable drums should be suitable for wheel mounting.

- STANDARD LENGTH:

The standard length of drum will be 500 meter with + 5%

Non-standard Length:

Nonstandard length not less than 50% of the standard length shall be accepted to the extent of 10% of the ordered quantity.

- INSPECTION:

All tests and inspections shall be made at the place of manufacturer unless otherwise especially agreed upon by the manufacturer and purchaser at the time of purchase. The manufacturer shall afford the inspector representing the purchaser all reasonable facilities, without charge, to satisfy him that the material is being furnished in accordance with this specification.

- EXPERIENCE:

The manufacturer must have some experience of manufacturer and supply of this cable to any Electricity Board. Copy of order executed and performance report may be submitted along with the offer.

- TYPE TEST CERTIFICATES:

The duly attested copy of Type Test Certificate of the offered sizes of AB cable, as per IS: 14255/1995 with latest amendment/revision be submitted from any Govt. laboratory or from a NABL accredited  laboratory along with the offer. Type Test Certificate shall not be more than Five Years Old from Date of supply.

However, if the same are not available at the time of bidding, the same  may be submitted after order  but before  commencement of supply.

In case,  the bidder  is not able to submit the Type Test Certificate from any Govt. laboratory or from a NABL accredited  laboratory   for any  size  of cable, the same shall be conducted by the bidder free of cost without any additional financial liability on utility.  For this purpose, Type test Report of a   phase wire or messenger wire once tested shall be accepted  for all other combination. Fro example,  if 1x16 + 25 sq mm  and 3x35 + 25 sq mm   already tested  then this will be valid  for 3x16+25 sq  mm   (as phase wire of 16 sq mm and messenger wire of 25 aq mm are already tested)  and  for  3x35 + 25 sq mm  + 16 sq mm  (as phase wire of  35 & 16 sq mm and messenger wire of 25 aq mm are already tested.

- SUBMISSION OF ISI LICENSE FOR IS14255:1995

The Manufacturer are required to submit duly attested photo copy of the valid ISI License up to the date of delivery for supply of these AB cables/wires and they should also submit GTP failing which, the offer would be ignored.

- IMPORTANT:

In absence of valid ISI License/GTP duly filled in/and copy of type test certificate of Govt. approved Laboratory, duly attested by authorized person, offer will be liable to be ignored without any further correspondence.

- ISI MARKING:

The material supplied shall be conforming to Indian Standard Specification and also with ISI marking as applicable and even after inspection of the lot, if the materials received at site is found without ISI marking, the lot shall be rejected and no further correspondence shall be entertained in this regard.

Exact details of  marking/embossing, color of outer sheath etc.   will be as per the detailed purchase order.

GUARANTEED TECHNICAL PARTICULARS (G.T.P.)

Technical information and Guaranteed Technical Particulars (G.T.P.) for LT Aerial Bunched Cable (XLPE insulated only) of sizes:

| 1.01 | 1X16 (Ph) + 1X25 (bare messenger cum neutral) SQ. MM. |
| --- | --- |
| 1.02 | 1X16 (Ph) + 1X25 (bare messenger cum neutral) + 1x16 (insulated Street lighting)SQ. MM. |
| 1.03 | 3X16(Ph)+1X25 (bare messenger cum neutral) SQ. MM. |
| 1.04 | 3 X 16(Ph) +1x25 (bare messenger cum neutral) + 1x16 (insulated Street lighting) SQ. MM. |
| 1.05 | 1X25(Ph)+1x25 (bare messenger cum neutral) SQ. MM. |
| 1.06 | 1X25(Ph) + 1X25 (bare messenger cum neutral) + 1x16 (insulated Street lighting) SQ. MM. |
| 1.07 | 3X25(Ph)+1X25 (bare messenger cum neutral) SQ. MM. |
| 1.08 | 3 X 25(Ph) +1x25 (bare messenger cum neutral) + 1x16 (insulated Street lighting) SQ. MM. |
| 1.09 | 1X35(Ph)+1X25 (bare messenger cum neutral) SQ. MM. |
| 1.10 | 1x35(Ph) + 1X25 (bare messenger cum neutral) + 1x16 (insulated Street lighting) SQ. MM. |
| 1.11 | 3X35(Ph)+1X25 (bare messenger cum neutral) SQ. MM. |
| 1.12 | 3X35 (Ph) + 1x25 (bare messenger cum neutral)+ 1x16 (insulated Street lighting) SQ. MM. |
| 1.13 | 3X50(Ph)+1X35 (bare messenger cum neutral) SQ. MM. |
| 1.14 | 3X50 (Ph)+1x35 (bare messenger cum neutral) +1x16 (insulated Street lighting) SQ. MM. |
| 1.15 | 3X95(Ph)+1X70 (bare messenger cum neutral) SQ. MM. |

1.16       3X95(Ph)+1X70 (bare messenger cum neutral) SQ. MM+1x16 (insulated Street lighting) SQ. MM

PART – A

Manufacturer has to confirm following important requirements:

| Sr. No. | Particulars | confirmation |  |
| --- | --- | --- | --- |
| 1 | AB Cable shall be manufactured and supplied Confirming to IS: 14255/1995 with latest Amendment if any | Yes |  |
| 2 | Cable drums/label shall bear ISI Mark | Yes |  |
| 3 | ISI License shall remain valid till order is Completed | Yes |  |
| 4 | Colour of XLPE Insulation – Black |  |  |
| 4a | 1X16 + 1X25 SQ. MM. | Yes |  |
| 4b | 1X16 + 1X25 + 1x16 SQ. MM. | Yes |  |
| 4c | 3X16+1X25 SQ. MM. | Yes |  |
| 4d | 3 X 16 +1x25 + 1x16 SQ. MM. | Yes |  |
| 4e | 1X25+1x25 SQ. MM. | Yes |  |
| 4f | 1X25 + 1X25 + 1x16 SQ. MM. | Yes |  |
| 4g | 3X25+1X25 SQ. MM. | Yes |  |
| 4h | 3 X 25 +1x25 + 1x16 SQ. MM. | Yes |  |
| 4i | 1X35+1X25 SQ. MM. | Yes |  |
| 4j | 1x35 + 1X25 + 1x16 SQ. MM. | Yes |  |
| 4k | 3X35+1X25 SQ. MM. | Yes |  |
| 4l | 3X35 + 1x25 + 1x16 SQ. MM. | Yes |  |
| 4m | 3X50+1X35 SQ. MM. | Yes |  |
| 4n | 3X50 +1x35 +1x16 SQ. MM. | Yes |  |
| 4o | 3X95+1X70 SQ. MM. | Yes |  |
| 5 | Shape – compacted | Yes |  |
| 6 | Standard length in case 500 mtrs+ 5 % tolerance longer length acceptable | Yes |  |
| 7 | Non-Standard length 50% of Std. length up to 10%of ordered quantity | Yes |  |
| 8 | Packing shall contain only one Length. | Yes |  |
| 9 | Packing material: Wooden drums as per IS: 10418/1982 duly painted | Yes |  |
| 9a | 1X16 + 1X25 SQ. MM. | Yes |  |
| 9b | 1X16 + 1X25 + 1x16 SQ. MM. | Yes |  |
| 9c | 3X16+1X25 SQ. MM. | Yes |  |
| 9d | 3 X 16 +1x25 + 1x16 SQ. MM. | Yes |  |
| 9e | 1X25+1x25 SQ. MM. | Yes |  |
| 9f | 1X25 + 1X25 + 1x16 SQ. MM. | Yes |  |
| 9g | 3X25+1X25 SQ. MM. | Yes |  |
| 9h | 3 X 25 +1x25 + 1x16 SQ. MM. | Yes |  |
| 9i | 1X35+1X25 SQ. MM. | Yes |  |
| 9j | 1x35 + 1X25 + 1x16 SQ. MM. | Yes |  |
| 9k | 3X35+1X25 SQ. MM. | Yes |  |
| 9l | 3X35 + 1x25 + 1x16 SQ. MM. | Yes |  |
| 9m | 3X50+1X35 SQ. MM. | Yes |  |
| 9n | 3X50 +1x35 +1x16 SQ. MM. | Yes |  |
| 9o | 3X95+1X70 SQ. MM. | Yes |  |
| 10 | Following shall be embossed on cable & Marking on drum shall be as per IS: 14255/1995 | Yes |  |
| 10a | Purchaser (Employee) | Yes |  |
| 10b | 1100 Volts | Yes |  |
| 10c | IS:14255/1995 | Yes |  |
| 10d | Year of manufacture | Yes |  |
| 10e | Trade Mark | Yes |  |
| 11 | Conductor – |  |  |
| 11a | For Phase 16 mm² ,25 mm², 35 mm², 50 mm² & 95 mm² Aluminium as per IS 8130/1984 | Yes |  |
| 11b | For Messenger wire 25 mm², 35 mm² & 70 mm² Aluminium Alloy as per IS 398/Pt.IV/1994 | Yes |  |
| 12 | Maximum Conductor resistance at 20ºC For Phase Conductor |  |  |
| 12a | 16 mm² Conductor – 1.91 Ohm/KM | Yes |  |
| 12b | 25 mm² Conductor – 1.20 Ohm/KM | Yes |  |
| 12c | 35 mm² Conductor – 0.868 Ohm/KM | Yes |  |
| 12d | 50 mm² Conductor – 0.641 Ohm/KM | Yes |  |
| 12e | 95 mm² Conductor – 0.320 Ohm/KM | Yes |  |
|  | For messenger conductor |  |  |
| 12e | 25 mm² Conductor – 1.380 Ohm/KM | Yes |  |
| 12f | 35 mm² Conductor – 0.986 Ohm/KM | Yes |  |
| 12g | 70 mm² Conductor – 0.492 Ohm/KM | Yes |  |
| 13 | Minimum average XLPE Insulation thickness for AB Cable |  |  |
| 13a | 16 mm² - 1.2 mm | Yes |  |
| 13b | 25 mm² - 1.2 mm | Yes |  |
| 13c | 35 mm² - 1.2 mm | Yes |  |
| 13d | 50 mm² - 1.5 mm | Yes |  |
| 13f | 95 mm² - 1.5 mm | Yes |  |
| 14 | Volume resistivity of insulation |  |  |
| 14a | At 27ºC – 1 x 10^13 Ohm-cm. Min | Yes |  |
| 14b | At 70°C – 1 x 10^11 Ohm-cm. Min | Yes |  |
| 15 | Tensile strength of Insulation & sheath -12.5 N/mm² Min. | Yes |  |
| 16 | Elongation at break of Insulation and Sheath –200% Min. | Yes |  |
| 17 | Overall tolerance in supply of ordered total quantity shall be + 2 %( Plus and minus two %) | Yes |  |

PART- B

Manufacturer has to furnish below details about material for information:

| Sr. No. | Particulars |  |  |  | confirmation |  |
| --- | --- | --- | --- | --- | --- | --- |
| 1 | ISI License for IS:14255/1995 |  |  |  | Yes |  |
| 1a | Number |  |  |  |  |  |
| 1b | Date of expiry |  |  |  |  |  |
| 2 | Approximate weight of 1000 meters length (Weightin Kgs.) |  |  |  |  |  |
| 2a | Size of cable | Alum. | Alu. Alloy | XLPE | Total |  |
|  | 1X16 + 1X25 SQ. MM. |  |  |  |  |  |
|  | 1X16 + 1X25 + 1x16 SQ. MM. |  |  |  |  |  |
|  | 3X16+1X25 SQ. MM. |  |  |  |  |  |
|  | 3 X 16 +1x25 + 1x16 SQ. MM. |  |  |  |  |  |
|  | 1X25+1x25 SQ. MM. |  |  |  |  |  |
|  | 1X25 + 1X25 + 1x16 SQ. MM. |  |  |  |  |  |
|  | 3X25+1X25 SQ. MM. |  |  |  |  |  |
|  | 3 X 25 +1x25 + 1x16 SQ. MM. |  |  |  |  |  |
|  | 1X35+1X25 SQ. MM. |  |  |  |  |  |
|  | 1x35 + 1X25 + 1x16 SQ. MM. |  |  |  |  |  |
|  | 3X35+1X25 SQ. MM. |  |  |  |  |  |
|  | 3X35 + 1x25 + 1x16 SQ. MM. |  |  |  |  |  |
|  | 3X50+1X35 SQ. MM. |  |  |  |  |  |
|  | 3X50 +1x35 +1x16 SQ. MM. |  |  |  |  |  |
|  | 3X95+1X70 SQ. MM. |  |  |  |  |  |
| 3 | Cable Conductor, Circular Compacted? |  |  |  | Yes |  |

PART – C (ENCLOSURES)

Manufacturers have to enclose following documents and has to confirm for the same

| Sr. No. | Particulars |  |  |  |  |  | confirmation |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | ISI License |  |  |  |  |  | Yes |  |
| 2 | Proof if applied for renewal of ISI License |  |  |  |  |  | Yes |  |
| 3 | TYPE TEST CERTIFICATE: Type test certificate from Govt. of India approved Laboratory |  |  |  |  |  | Yes |  |
|  | Size of AB Cable |  |  |  |  |  |  |  |
|  | a | Name of Lab. & City Name |  |  |  |  |  |  |
|  | b | T.R. No. |  |  |  |  |  |  |
|  | c | Date |  |  |  |  |  |  |
| 4 | List of plant and machinery |  |  |  |  |  | Yes |  |
| 5 | List of testing facility available |  |  |  |  |  | Yes |  |
| 6 | List of orders pending/executed |  |  |  |  |  | Yes |  |
| 6a | with Employer |  |  |  |  |  | Yes |  |
| 6b | with agencies other than Sr. no. 6(a) |  |  |  |  |  | Yes |  |