SCOPE

This specification covers requirements of XLPE Insulated 11 kV Aerial

Bunched Cables for overhead lines

- COMPOSITION OF THE CABLE

The   composite cable shall compose three single –core cables twisted around a bare aluminium alloy messenger wire ,which will carry the weight of the cable.

- RATED VOLTAGE

The rated voltage of the cables shall be 6.35/11lV and the maximum operating voltage shall be 12kV

- APPLICABLE STANDARDS

Unless otherwise stipulated in this specification ,the following standards shall be applicable.

- IS:-7098(Part-2)-2011-Cross linked Polyethylene Insulated PE

sheathed Cable

- IS: 8130-2013 –Conductors for Insulated cables.

- IS :398(Part-IV)-1994- Aluminum Alloy Conductors

5.0   CONSTRUCTION OF CABLE

“Stranded Compacted Circular Aluminum conductor, Extruded layer of semiconducting      compound, XLPE Insulated, Insulation Shielding with Extruded layers of semiconducting compound & Metallic Tape ,PE /PVC Sheathed Overall. Three Phase Cores shall be twisted around Bare/Insulated Stranded Messenger Conductor”.

- DETAILS OF SINGLE CORE CABLE

6.1    Conductor

The cable conductor shall be round, stranded & compacted aluminum of nominal cross sectional area of 35mm² to 240 mm² meeting all  requirement as per IS-8130/2013.

6.2    Conductor Screen

The conductor screen shall be of extruded semi conducting cross linked polyethylene   compound of thickness not less than 0.5 mm.

6.3   Insulation

The Insulation shall be of extruded cross linked polyethylene (XLPE)  &

Nominal insulation thickness 3.6 mm & its properties shall conform to IS

7098(Part-2)/2011

6.4 Insulation Screen

a) Non-Metallic Part

Insulation screened shall comprise extruded semiconducting compound

of thickness shall be not less than 0.6 mm.

b) Metallic Part

The Metallic Screen shall consist of Copper tape semiconducting

layer with overlap. Thickness of Copper tape shall not less than 0.06

mm

6.5 Outer Sheath

The Outer sheath shall be of black Polyethylene conforming to requirement as per Table-3 of IS: 7098 (Part-2)/2011 or black PVC conforming to requirement of Type ST2 of IS:5831.The Nominal thickness of sheath shall be as per Table-7 of IS: 7098 (Part-2)/2011

Note: -A barrier between Metallic part of screen & Outer sheath may be applied at the discretion of manufacturer.

7.0   MESSENGER (NEUTRAL CONDUCTOR)

The bare messenger wire shall be of aluminium alloy generally confirming to IS-398(Part-IV)-1994,comprising of 7 strands upto  95sqmm & 19 strands  above 95sqmm and shall be stranded Compacted or uncompacted circular to have smooth round surface to avoid damage to the outer insulating sheath of single core phase cables twisted around messenger.

There shall be no joints in any wire of the stranded messenger conductor except those made in the base rod or wire before finally drawing.

The technical characteristics of messenger wire shall be as follows.

| Nominal Cross Sectional Area of Phase Conductor (Sqmm) | Aluminum Alloy Stranded Messenger Conductor |  |  |  |
| --- | --- | --- | --- | --- |
|  | Nominal Cross Sectional Area of Messenger (Sqmm) | No. of Strands | Max. D.C. Resistance of Messenger at 20ºC (Ohm/km) | Min. Breaking Load of Messenger (kN) |
| 35 | 50 | 7 | 0.689 | 14.0 |
| 50 | 50 | 7 | 0.689 | 14.0 |
| 70 | 70 | 7 | 0.492 | 19.7 |
| 95 | 70 | 7 | 0.492 | 19.7 |
| 120 | 95 | 7 | 0.363 | 26.7 |
| 150 | 120 | 19 | 0.287 | 33.8 |
| 185 | 150 | 19 | 0.230 | 42.2 |
| 240 | 185 | 19 | 0.186 | 52.1 |

Note: The value of D.C Resistance is to be guaranteed . A tolerance of

(-)5% is permissible on the value of Breaking load .

8.     Recommended Thickness of PE /PVC covering for messenger conductor

| Nominal Cross Sectional Area (Sqmm) | Nominal Thickness (mm) |
| --- | --- |
| 50 | 1.20 |
| 70 | 1.50 |
| 95 | 1.50 |
| 120 | 1.80 |
| 150 | 1.80 |
| 185 | 2.00 |

8       PHASE IDENTIFICATION Shall be done by Ridges One ,Two & Three for Three Phase on  sheath  & Colour Strip of Red, Yellow & Blue shall be applied longitudinally  under copper tape

- CABLE DRUM

  - A B Cables shall be supplied non   returnable wooden drums of heavy construction

conforming to IS : 10418. Wooden drum shall be properly seasoned sound and free from defects. Wood preservative shall be applied to the entire drum.

  - Standard lengths cables shall be 250/500 meters. The cable length per drum

shall be subject to a tolerance of plus or minus 5% of the standard drum length.  The owner shall have the option of rejecting cable drums with shorter lengths. However, the total quantity of cables after taking into consideration of all cable drums for each size shall be within the tolerance of ± 2%.

  - A clear space of at least 40 mm shall be left between the cables and the lagging.

  - Each drum shall carry the manufacturer's name, the purchaser's name, address and contract number and type, size and length of the cable, net and gross weight and year of manufacture stencilled on both sides of drum.  A tag containing the same information shall be attached to the leading end of the cable.  An arrow and suitable accompanying wording shall be marked on one end of the reel indicating the direction in which it should be rolled.

  - Packing shall be sturdy and adequate to protect the cables, from any injury due to mishandling or other conditions encountered during transportation, handling and storage.  Both cable ends shall be sealed with PVC/Rubber caps so as to eliminate ingress of water during transportation and erection.

- TESTS

  - Type Test

Following shall constitute type test as per IS: 7098 Part-II/2011

- Test on Phase conductor

  - Tensile Test

  - Wrapping Test

  - Resistance Test

- Test on Messenger conductor

  - Breaking load

  - Resistance test

- Physical Test for XLPE insulation

  - Tensile strength and elongation at break

  - Ageing in air oven

  - Hot set test

  - Shrinkage test

  - Water absorption (Gravimetric)

- Physical test for PE sheath as per table 3 of IS:7098 Part-2/2011

- Insulation resistance(volume resistivity) test

- High voltage test

- Heating Cycle test

- Partial Discharge test

- Bending test

- Dielectric Power factor test

i)As a function of voltage

ii)As a function of temperature

  - Acceptance Tests

Following shall constitute acceptance test as per IS:7098 Part-II/2011

- Tensile test for phase conductor

- Wrapping test for phase conductor

- Breaking load for messenger conductor

- Conductor resistance test

- Test for thickness of insulation

- Tensile strength and elongation at break

- Hot set test for XLPE insulation

- Insulation resistance test

- High voltage test

- Partial Discharge test

  - Routine Tests

Following shall constitute routine test as per IS:7098 Part-II/2011

- Conductor resistance test

- High voltage test

- Partial Discharge test

  - Test on Messenger Conductor

- D.C. Resistance

- Breaking Load

- Thickness of Insulation(As agreed at the time of tendering for Insulated messenger conductor)

- No. Of Strands.

Sample Batch for Type Testing

  - The Supplier shall offer material for selection of samples for type testing only after getting Quality Assurance plan approved from Owner’s Quality Assurance Deptt. The sample shall be manufactured strictly in accordance with the Quality Assurance Plan approved by Owner.

  - The Supplier shall offer at least three drum for selection of sample required for conducting

all the type test.

  - The Supplier is required to carry out all the Acceptance tests successfully in presence of Owner’s representative before sample selection.