# ACSR CONDUCTOR

#### SCOPE

This section covers design, manufacture, testing before dispatch, packing, supply and delivery to  destination of   ACSR  Squirrel, Weasel,  Rabbit, Racoon,  Dog  and  Panther Conductor.

#### STANDARDS

The Conductor shall also comply in all respects with the IS: 398(Part-II)-1996 with latest amendments unless otherwise stipulated in this specification or any other International Standards which ensure equal or higher quality material.

The ACSR Conductor shall also conform to the following standards.

| Sl. No. | Indian Standards | Title | International |
| --- | --- | --- | --- |
| 1 | IS:209-1979 | Specification for Zinc | BS-3436-1961 |
| 2 | IS:398-1996 | Specification for aluminum conductors for overhead transmission purposes. |  |
|  | Part-II | Aluminum conductors | IEC-209-1966 |
|  |  | Galvanized steel reinforced | BS-215(Part-II) |
| 3 | IS:1521-1972 | Method of Tensile Testing of Steel wire | ISO/R89-1959 |
| 4 | IS:1778-1980 | Reels and Drums for Bare conductors | BS-1559-1949 |
| 5 | IS:1841-1978 | E.C. Grade Aluminum rod produced by rolling |  |
| 6 | IS:2629-1966 | Recommended practice for Hot Dip Galvanizing of iron and steel |  |
| 7 | IS:2633-1986 | Method of testing uniformity of coating of zinc coated articles. |  |
| 8 | IS:4826-1968 | Galvanized coatings on round steel wires. | ASTM A472-729 |
| 9 | IS:5484-1978 | E.C. Grade Aluminium rod produced by continuous casting and rolling. |  |
| 10 | IS:6745-1972 | Methods of determination of weight of zinc-coating of zinc coated iron and steel articles | BS-443-1969 |

Offersconforming to standards other than IS-398 shall be accompanied by the English version of relevant standards in support of the guaranteed technical particulars to be furnished as per format enclosed.

#### GENERAL TECHNICAL REQUIREMENTS

The General Technical Requirements are given in Section-II. The Conductor shall conform to these  technical requirements.

The Bidder shall furnish guaranteed technical particulars in Section-III.

#### MATERIALS/WORKMANSHIP

    - The material offered shall be of best quality and workmanship. The steel coredaluminum conductor strands shall consist of hard drawn aluminium wire manufactured from not less than 99.5% pure electrolytic aluminium rods of E.C. grade and copper content not exceeding 0.04%. They shall have the same properties and characteristics as prescribed in IEC: 889- 1987. The steel wire shall be made from material produced either by the acid or basic open hearth process or by electric furnace process or basic oxygenprocess. Steel wire drawn from Bessemer process shall not be used.

    - The steel wires shall be evenly and uniformly coated with electrolytic high grade, 99.95% purity zinc complying with the latest issue of IS-209 for zinc. The uniformity of zinc coating and the weight of coating shall be in accordance with Section-II and shall be tested and determined according to the latest IS-2633 or any other authoritative standard.

    - The steel strands shall be hot dip galvanized as per IS: 4826. The coating shall be smooth, continuous, and of uniform thickness,free from imperfections and shall withstand minimum three dips after stranding in standard preece test. The steel strands shall be preformed and postformed in order to prevent spreading of strands in the event of cutting of composite core wire. The properties and characteristics of finished strands and individual wires shall be as prescribed in IEC: 888- 1987.

If tested  after stranding, reference  shall also be made  to cl. 4.1.1 and cl. 4.2.3 of IS : 4826.

#### CONDUCTOR PARAMETERS

The Parameters of individual strands and composite steel coredaluminumconductor, shall be in accordance with the values given in Section-II.

Creep in a conductor is attributed partly due to settlement of strands and partly due to non-elastic elongation of metal when subjected to load. The manufacturer of conductor shall furnish the amount of creep which will take place in 10, 20, 30, 40 and 50 years along with the supporting calculations. The calculations should be based on everyday temperature of 32 ºC and everyday tension of 25% of UTS of conductor of 11/33 KV Lines.

#### TOLERANCES

The tolerances on standard diameter of Aluminum and Steel wires shall be as detailed in specific technical requirements.

The cross-section of any wire shall not depart from circularity by more than an amount corresponding to the tolerance on the standard diameter.

The details of diameters, lay ratios of Aluminum and steel wires shall be in accordance with the Section-II "Technical Requirements".

#### SURFACE CONDITIONS

All aluminum and steel strands shall be smooth, and free from all imperfections, spills/and splits. The finished conductor shall be smooth, compact, uniform and free from all imperfections including spills and splits, die marks, scratches, abrasions, scuff marks, kinks (protrusion of wires), dents, pressmarks, cut marks, wire cross-over, over-riding looseness, pressure and/or unusual bangle noise on tapping, material inclusions, white rust, powder formation or black spots (on account of reaction with trapped rain water etc.,), dirt, grit, etc. The surface of conductor shall be free from points, sharp edges, abrasions or other departures from smoothness or uniformity of surface contour that would increase radio interference and corona losses. When subjected to tension upto 50% of  the  ultimate strength of the conductor, the surface shall not depart from the cylindrical form nor any part of the component parts or strands move relative to each other in such a way as to get out of place and disturb the longitudinal smoothness of the conductor.

#### JOINTS IN WIRES

  - Aluminum wires

During stranding, no aluminum wire welds shall be made for the purpose of achieving the required conductor length.

No joint shall be permitted in the individual aluminum wires in the outer most layer of the finished Conductor. However, joints in the 12 wire & 18 wire inner layer of the conductor are permitted but these joints shall be made by the cold pressure butt welding and shall be such that no two such joints shall be within 15 meters of each other in the complete stranded conductor.

#### Steel wires

There shall be no joints in finished steel wires forming the core of the steel reinforced aluminum conductor.

#### STRANDING

The wires used in construction of the stranded conductor, shall, before stranding, satisfy all requirements of IS-398 (Part-II) 1996.

In all constructions, the successive layers shall be stranded in opposite directions. The wires in each layer shall be evenly and closely stranded round the underlying wire or wires. The outer most layer of wires shall have a right hand lay. The lay ratio of the different layers shall be within the limits given under Section-II.

#### PACKING

  - The conductor shall be supplied in non-returnable strong wooden drums provided with lagging of adequate strength constructed to protect the conductor against any damage and displacement during transit, storage and subsequent handling and stringing operations in the field. The drums shall generally conform to IS-1778-1980 and latest version except as otherwise specified hereinafter. The conductor drums shall be adequate to wind one or more standard length of 2500 meters of SQUIRREL/WEASEL/RABIT/RACOON/DOG/ PANTHER ACSR conductor.

  - The drums shall be suitable for wheel mounting and for letting off the conductor under a minimum controlled tension of the order of 5KN. The conductor drums shall be provided with necessary clamping arrangements so as to be suitable for tension stringing of power conductor.

  - The bidders should submit their drawings of the conductor drums along with the bid. After placement of letter of intent the Manufacturer shall submit four copies of fully dimensioned

drawing of the drum for Employer's approval. After getting approval from the Employer, Manufacturer shall submit 30 more copies of the approved drawings for further distribution and field use.

  - All wooden components shall be manufactured out of seasoned soft wood free from defects that may materially weaken the component parts of the drums. Preservative treatment for anti-termite/anti fungus shall be applied to the entire drum with preservatives of a quality which is not harmful to the conductor.

  - All flanges shall be 2-ply construction with 64 mm thickness. Each ply shall be nailed and clenched together at approximately 90 degrees. Nails shall be driven from the inside face of the flange, punched and then clenched on the outer face. Flange boards shall not be less than the nominal thickness by more than 2 mm. There shall not be less than 2 nails per board in each circle.

  - The wooden battens used for making the barrel of the conductor shall be of segmental type. These shall be nailed to the barrel supports with at least two nails. The battens shall be closely butted and shall provide a round barrel with smooth external surface. The edges of the battens shall be rounded or chamfered to avoid damage to the conductor.

  - Barrel studs shall be used for construction of drums. The flanges shall be holed and the barrel supports slotted to receive them. The barrel studs shall be threaded over a length on either end, sufficient to accommodate washers, spindle plates and nuts for fixing flanges at the required spacing.

  - Normally, the nuts on the studs shall stand protruded of the flanges. All the nails used on the inner surface of the flanges and the drum barrel shall be countersunk. The ends of the barrel shall generally be flushed with the top of the nuts.

  - The inner cheek of the flanges and drum barrel surface shall be painted with bitumen based paint.

  - Before reeling, card board or double corrugated or thick bituminized waterproof bamboo paper or HDPE sheet  shall be secured to the drum barrel and inside of flanges of the drum by means of a suitable commercial adhesive material. The paper should be dried before use.  After reeling the conductor the exposed surface of the outer layer of conductor shall be wrapped with thin polythene sheet across the flanges to preserve the conductor from dirt, grit and damage during transportation and handling and also to prevent ingress of rain water during storage/transport.

  - A minimum space of 75 mm shall be provided between the inner surface of the external protective lagging and outer layer of the conductor. Outside the protective lagging, there shall be minimum of two binders consisting of hoop iron/galvanised steel wire. Each protective lagging shall have two recesses to accommodate the binders.

  - Each batten shall be securely nailed across grains as far as possible to the flange edges with at least 2 nails per end. The length of the nails shall not be less than twice the thickness of the battens. The nail shall not protrude above the general surface and shall not have exposed sharp edges or allow the battens to be released due to corrosion.

  - The conductor ends shall be properly sealed and secured with the help of U-nails on one side of the flanges.

  - Only standard lengths of conductor shall be wound on each drum. The method of lagging to be employed shall be clearly stated in the tender.

  - As an alternative to wooden drum Bidder may also supply the conductors in non-returnable

painted steel drums. The painting shall conform to IS:9954-1981,reaffirmed in 1992. Wooden/ steel drum will be treated at par for evaluation purpose and accordingly the Bidder should quote the package.

#### LABELLING AND MARKING

The drum number shall be branded or gauged or stencilled into the flange. An arrow shall be marked on the sides of the drum, together with the words "Roll this way". Each drum shall have the following information provided on the outside of the flange stencilled with indelible ink.

- Manufacturer's name and address.

- Contract/Specification number.

- Size and type of conductor.

- Net weight of the conductor.

- Gross weight of the conductor and drum.

- Length of the conductor.

- Position of the conductor end.

- Drum and lot number.

- Name and address of the consignee.

- Month and year of manufacture.

- The drum may also be marked with standard specification as per which the  conductor is manufactured.

#### STANDARD LENGTHS

  - The standard length of the conductor shall  be 2500 metres. A tolerance of plus or minus 5% on the standard length offered by the bidder shall be permitted. All lengths outside this limit of tolerance shall be treated as random lengths.

  - Random lengths will be accepted provided no length is less than 70% of the standard length and total quantity of such random length shall not be more than 10% of the total quantity order. When one number random length has been manufactured at any time, five (5) more individual lengths, each equivalent to the above random length with a tolerance of +/-5% shall also be manufactured and all above six random lengths shall be dispatched in the same shipment. At any point, the cumulative quantity supplied including such random lengths shall not be more than 12.5% of the total cumulative quantity supplied including such random lengths. However, the last 20% of the quantity ordered shall be supplied only in standard length as specified.

  - Bidder shall also indicate the maximum single length, above the standard length, he can manufacture in the guaranteed technical particulars of offer. This is required for special stretches like river crossing etc. The Employer reserves the right to place orders for the above lengths on the same terms and conditions applicable for the standard lengths during the pendency of the Contract.

#### QUALITY ASSURANCE PLAN

A Quality Assurance Plan including customer hold points covering the manufacturing activities of the material shall be required to be submitted by the tenderer to the Employer along with the tender. The Quality Assurance Plan after the same is found acceptable, will be approved by the Employer.

The contractor shall follow the approved Quality Assurance Plan in true spirit. If desired by the Employer, he shall give access to all the documents and materials to satisfy the Employer that the Quality Assurance Plan is being properly followed.

#### TESTING

  - SELECTION OF TEST SAMPLES FOR TYPE TESTS

    - The samples shall be taken from a continuous length of conductor and subjected to all the tests specified in clause 14.

  - SELECTION OF TEST SAMPLES FOR ACCEPTANCE TESTS

    - Before dispatch from the works individual wire and finished steel coredaluminum conductor shall be subjected to the tests as specified in IS:398 or any other authoritative standard.

    - Sample for individual wires for test shall be taken before stranding from outer ends of not less than ten per cent of the spools in the case of aluminum wire and ten per cent of the wire coils in the case of steel wires. If samples are taken after stranding, they shall be obtained by cutting 1.2 meters from the outer ends of the finished conductor from not more than 10 per cent of the finished reels.

    - The routine tests shall be same as acceptance test. The manufacturer  will draw  samples  for  routine tests  as per  Cl. 13.1.1 or 13.1.2  of IS: 398 (Part 2)  and will maintain the record of routine tests  for buyer’s review.  For acceptance  tests, the sample  shall be taken as per Cl. shall be as per   Cl.  13.1.2 of IS: 398 (Part 2).

#### TESTS

The following tests shall be carried out on sample/samples of conductor.

#### Type Tests

    - Visual examination

    - Measurement of diameters of individual aluminum and steel wires.

    - Measurement of lay ratio of each layer

    - Breaking load test

    - Ductility test

    - Wrapping test

    - Resistance test on aluminum wires.

    - DC resistance Test on Aluminium Wires.

    - Galvanizing test

    - Surface condition test(applicable only  for  conductors of nominal aluminium area 100 sq. mm and above)

    - Stress Strain test

    - Procedure qualification test on welded joint of Aluminum Strands.

NOTE:-The type test reports shall not be older than FIVE years and shall be valid up to expiry of validity of offer.

The above additional lists if not conducted earlier, shall be done under the subject project package at no extra cost.

#### Acceptance tests and Routine tests

- Visual and dimensional check on drum.

- Visual examination

- Measurement of diameters of individual aluminum and steel wires.

- Measurement of lay ratio of each layer

- Breaking load test

- Ductility test

- Wrapping test

- Resistance test on aluminum wires.

- DC resistance Test on Aluminium Wires.

- Galvanizing test

#### Tests During Manufacture

The following tests during manufacture shall be carried out.

    - Chemical analysis of zinc used for galvanising,

    - Chemical analysis of aluminum used for making aluminumstrands,

    - Chemical analysis of steel used for making steel strands,

#### Visual examination

The conductor shall be examined visually for good workmanship and general surface finish of the conductor. The conductor drums shall be rewound in the presence of Inspecting Officer. The Inspector will initially check for Scratches, Joints etc., and that the conductor shall generally conform to the requirements of the specifications/IS 398(Part- II)-1996.

#### Measurement of diameters of individual Aluminum and Steel Wires.

The diameters of individual Aluminum and Steel Wires shall be checked to ensure that they conform to the requirements of this specification.

#### Measurement of lay-ratios

The lay-ratios of each layer of the conductor shall be measured and checked to ensure that they conform to the requirements of this specification and IS:398 (Part-II)-1996.

#### Breaking load test

- Breaking load test on complete conductor.

Circles perpendicular to the axis of the conductor shall be marked at two places on a sample of conductor of minimum 5m length between fixing arrangement suitably fixed on a tensile testing machine. The load shall be increased at a steady rate upto 50% of minimum specified UTS and held for one minute. The circles drawn shall not be distorted due to relative movement of strands. Thereafter the load shall be increased at steady rate to 100% of UTS and held for one minute. The Conductor sample shall not fail during this period. The applied load shall then be increased until the failing load is reached and the value recorded.

#### Breaking load test on individual Aluminum and Galvanized steel wires.

This test shall be conducted on both Aluminum and Galvanized steel wires. The breaking load of one specimen cut from each of the samples taken shall be determined by means of suitable tensile testing machine. The load shall be applied gradually and the rate of separation of the jaws of the testing machine shall be not less than 25 mm/min. and not greater than 100 mm. / min. The ultimate breaking load of the specimens shall be not less than the values specified in the Section-II.

#### Ductility Test

For the purpose of this test both torsion and elongation tests shall be carried out on galvanized steel wires only.

#### Torsion Test

One specimen cut from each of the samples taken shall be gripped in two vices exactly 15 cms. apart. One of the vices shall be made to revolve at a speed not exceeding one revolution per second and the other shall be capable of moving longitudinally to allow for contraction or expansion during testing. A small  tensile load not exceeding 2 (two)

percent of the breaking load of the wire shall be applied to the samples during testing. The test shall be continued until fracture occurs and the fracture shall show a smooth surface at right angles to the axis of the wire. After fracture, the specimen shall be free from helical splits. The sample shall withstand a number of twists equivalent to not less than 18 on length equal to 100 times the diameter. When twisted after stranding the number of complete twists before fracture occurs shall be not less than 16 on a length equal to 100 times the diameter of the wire. In case test sample length is less or more than 100 times the stranded diameter of the strand, the minimum number of twists will be proportioned to the length and if number comes in the fraction then it will be rounded off to the next higher whole number. The fracture shall show a smooth surface at right angles to the axis of the wire.

#### Elongation Test

The elongation of one specimen cut from each of the samples taken shall be determined. The specimen shall be straightened by hand and an original gauge length of 200 mm. shall be marked on the wire. A tensile load shall be applied as described in 1.1.4.6.2.1 and the elongation shall be measured after the fractured ends have been fitted together. If the fracture occurs outside the gauge marks, or within 25 mm. of either mark and the required elongation is not obtained, the test shall be disregarded and another test conducted. When tested before stranding, the elongation shall be not less than 4 percent and when tested after stranding, the elongation shall be not less than 3.5 percent.

#### Wrapping Test

This test shall be conducted on both Aluminum and Galvanized steel wires.

    - Aluminum wires

One specimen cut from each of the samples of aluminum wires shall be wrapped round a wire of its own diameter to form a close helix of 8 turns. Six turns shall then be unwrapped and closely wrapped in the same direction as before. The wire shall not break or show any crack.

    - Galvanized steel wires

One specimen cut from each of the samples of galvanized steel wire taken shall be wrapped round a mandrel of diameter equal to 4 times the wire diameter to form a close helix of 8 turns. Six turns shall then be unwrapped and again closely wrapped in the same direction as before. The wire shall not break.

#### Resistance Test

This test shall be conducted on aluminum wires only, conforming to procedure as per IEC:889. The electrical resistance of one specimen of aluminum wire cut from each of the samples taken shall be measured at ambient temperature. The measured resistance shall be corrected to the value corresponding to 20 degrees C. by means of following formula.

1

R20 = RT------------------------

1+ alpha x (T-20) Where

R20 = Resistance corrected at 20 degrees C.

RT = Resistance measured at T degrees C.

alpha = Constant mass temperature coefficient ofresistance 0.004. T = Ambient temperature during measurement

This resistance calculated to 20 degrees C. shall be not more than the maximum value

specified in section-II.

#### Galvanizing Test

This test shall be conducted on galvanized steel wires only. The uniformity of Zinc coating and the weight of coating shall be in accordance with IS 4826-1979.

#### Surface Condition Test

A sample of the finished conductor for use in 11/33 KV system having a minimum length of 5 meters with compression type dead end clamps compressed on both ends in such manner as to permit the conductor to take its normal straight line shape, shall be subjected to a tension of 50 percent of the UTS of the conductor. The surface shall not depart from its cylindrical shape nor shall the strands move relative to each other so as to get out of place or disturb the longitudinal smoothness of conductor. The measured diameter at any place shall be not less than the sum of the minimum specified diameters of the individual aluminum and steel strands as indicated in Section-II.

#### Stress-Strain Test

#### (applicable only  for  conductors of nominal aluminium area 100 sq. mm and above)

The test is contemplated only to collect the creep data of the conductor from the manufacturer. A sample of conductor of minimum 10 meters length shall be suitably compressed with dead end clamps.

#### TEST SET-UP

  - The test sample shall be supported in a trough over its full length and the trough adjusted so that theconductor will not be lifted by more than 10mm under tension. This shall be ascertained by actual measurement.

  - The distance between the clamp and the sleeve mouth shall be monitored with callipers during the test to ensure that, after the test, it does not change by more than 1mm + 0.1mm from the value before the test.

  - The conductor strain shall be evaluated from the measured displacements at the two ends of the gauge length of the sample. The gauge reference targets shall be attached to the clamps which lock the steel and aluminum wires together. Target plates may be used with dial gauges or displacement transducers and care shall be taken to position the plates perpendicular to the conductor. Twisting the conductor, lifting it and moving it from side- to-side by the maximum amounts expected during the test should introduce no more than 0.3mm error in the reading.

#### TEST LOADS FOR COMPLETE CONDUCTOR

The loading conditions for repeated stress-strain tests for complete conductor shall be as follows:

  - 1KN load shall be applied initially to straighten the conductor. The load shall be removed after straightening and then the strain gauges are to be set At zero tension.

  - For non-continuous stress-strain data, the strain readings at 1KN intervals at  lower tensions and 5 KN intervals above 30% of UTS shall be recorded.

  - The sample shall be reloaded to 30% of UTS and held for 1 hour. Readings are to be noted after 5, 10, 15, 30, 45 and 60 minutes during the hold period. The load shall be released then after the hold period.

  - The sample shall be reloaded to 50% of UTS and held for 1 hour. Readings are to be noted after 5, 10, 15, 30, 45 and 60 minutes during the hold period. The load shall be released then after the hold period.

  - Reloading upto 70% of UTS shall be done and held for 1 hour. Readings are to be noted after 5, 10, 15, 30, 45 and 60 minutes. The load shall be released.

  - Reloading upto 85% of UTS shall be done and held for 1 hour. Readings are to be noted after 5, 10,15, 30, 45 and 60 minutes and the load shall be released then.

  - Tension shall be applied again and shall be increased uniformly until the actual breaking strength is reached. Simultaneous readings of tension and elongation shall be recorded upto 90% of UTS at the intervals described under Clause 16.6.

#### TEST LOADS FOR STEEL CORE ONLY

#### (applicable only  for  conductors of nominal aluminium area 100 sq. mm and above)

The loading conditions for repeated stress-strain tests for the steel core of ACSR shall be as follows:

  - The test shall consist of successive applications of load applied in a manner similar to that for the complete conductor at 30%, 50%, 70% and 85% of UTS.

  - The steel core shall be loaded until the elongation at the beginning of each hold period corresponds to that obtained on the complete conductor at 30%, 50%, 70% and 85% of UTS respectively.

#### STRESS-STRAIN CURVES

The design stress-strain curve shall be obtained by drawing a smooth curve through the

0.5 and 1 hour points at 30%,50% and 70% of UTS loadings. The presence of any aluminum slack that can be related to any observed extrusion entering the span from the compression dead ends shall be removed from the lower ends of the design curves. Both the laboratory and standard stress-strain curves shall be submitted to the Employeralongwith test results. The stress-strain data obtained during the test shall be corrected to the standard temperature i.e. 20 deg.C.

#### DC RESISTANCE TEST ON COMPOSITE CONDUCTOR

On a conductor sample of minimum 5m length, two contact clamps shall be fixed with a pre-determined bolt torque. The resistance of the sample shall be measured by a Kelvin double bridge by placing the clamps initially zero meter and subsequently one meter apart. The test shall be repeated at least five times and the average value recorded. The value obtained shall be corrected to the value at 20 deg C as per clause no. 12.8 of IS:398 (Part-II)-1982/1996.The corrected resistance value at 20 deg.C shall conform to the requirements of this specification.

#### PROCEDURE QUALIFICATION TEST ON WELDED ALUMINUM STRANDS.

Two Aluminum wires shall be welded as per the approved quality plan and shall be subjected to tensile load. The breaking strength of the welded joint of the wire shall not be less than the guaranteed breaking strength of individual strands.

- CHEMICAL ANALYSIS OF ALUMINUM AND STEEL

Samples taken from the Aluminum and Steel ingots / coils/ strands shall be chemically/ spectrographicallyanalyzed. The same shall be in conformity with the requirements stated in this specification.

- CHEMICAL ANALYSIS OF ZINC

Samples taken from the zinc ingots shall be chemically / spectrographically analysed.The same shall be in conformity with the requirements stated in this specification.

- VISUAL AND DIMENSIONAL CHECK ON DRUMS

The drums shall be visually and dimensionally checked to ensure that they conform to the requirements of this specification.

- REJECTION AND RETEST

  - In case of failure in any type test, the Manufacturer is either required to manufacture fresh sample lot and repeat all the tests successfully once or repeat that particular type test three times successfully on the sample selected from the already manufactured lot at his own expenses. In case a fresh lot is manufactured for testing then the lot already manufactured shall be rejected.

  - If samples are taken for test after stranding and if any selected reel fails in the retest, the manufacturer may test each and every reel and submit them for further inspection. All rejected material shall be suitably marked and segregated.

- CHECKING AND VERIFICATION OF LENGTH OF CONDUCTOR

The contractor should arrange for inspection by the representative of the Employer specially authorised for this purpose. At least 50% of the total number of drums of conductor subject to minimum of two taken at random should be checked to ascertain the length of conductor. Arrangements should be made available in the works of the manufacturer for transferring the conductor from one reel to another at the same time measuring the length of the conductor so transferred by means of a meter.

- ADDITIONAL TESTS

The Employer reserves the right of having at his own expenses any other test(s) of reasonable nature carried out at Bidder's premises, at site, or in any other standard Laboratory in addition to the aforesaid type, acceptance and routine tests to satisfy himself that the materials comply with the specifications.

- TESTING EXPENSES

  - The breakup of the testing charges for the type tests specified shall be indicated separately.

  - Bidder shall indicate the laboratories in which they propose to conduct the type test. They shall ensure that adequate facilities are available in the laboratories and the tests can be completed in these laboratories within the time schedule guaranteed by them.

  - The entire cost of testing for the acceptance and routine tests and tests during manufacture specified herein shall be treated as included in the quoted unit price of the conductor, except for the expenses of the inspector/Employer's representative.

  - In case of failure in any type test, if repeat type tests are required to be conducted then

all the expenses for deputation of Inspector/Employer's representative shall be deducted from the contract price. Also if on receipt of the Manufacturer's notice of testing, the Employer's representative does not find 'plant' to be ready for testing, the expenses incurred by the Employer for re-deputation shall be deducted from contract price.

- TEST REPORTS

  - Copies of type test reports shall be furnished in at least six copies alongwith one original. One copy will be returned duly certified by the Employer only after which the commercial production of the material shall start.

  - Record of Routine test reports shall be maintained by the Manufacturer at his works for periodic inspection by the Employer's representative.

  - Test certificates of Tests during manufacture shall be maintained by the Manufacturer. These shall be produced for verification as and when desired by the Employer.

- TEST FACILITIES

The following additional test facilities shall be available at the Manufacturer's works:

- Calibration of various testing and measuring equipment including tensile testing machine, resistance measurement facilities, burette, thermometer, barometer etc.

- Standard resistance for calibration of resistance bridges.

- Finished Conductor shall be checked for length verification and surface finish on separate rewinding machine at reduced speed(variable from 8 to 16 meters per minute).The rewinding facilities shall have appropriate clutch system and be free of vibrations, jerks etc with traverse laying facilities.

- INSPECTION

  - The Employer's representative shall, at all times, be entitled to have access to the works and all places of manufacture where conductor shall be manufactured and the representative shall have full facilities for unrestricted inspection of the Bidder's works, raw materials and process of manufacture and conducting necessary tests as detailed herein.

  - The Bidder shall keep the Employer informed in advance of the time of starting and of the progress of manufacture of conductor in its various stages so that arrangements can be made for inspection.

  - The contractor will intimate the Employer about carrying out of the tests at least 45 days in advance of the scheduled date of tests during which the Employer will arrange to depute his representative/s to be present at the time of carrying out of the tests. Six (6) copies of the test reports shall be submitted.

  - No material shall be dispatched from its point of manufacture before it has been satisfactorily inspected and tested, Unless the inspection is waived off by the employer in writing. In the later case also, the conductor shall be dispatched only after satisfactory testing for all tests specified herein has been completed and approved by the employer.

  - The acceptance of any quantity of material shall in no way relieve the Bidder of any of his responsibilities for meeting all requirements of the specification, and shall not prevent subsequent rejection if such material is later found to be defective.

  - At least 50% of the total number of drums subject to minimum of two in any lot put up for inspection, shall be selected at random to ascertain the length of conductor by the following method:

"At the works of the manufacturer of the conductor, the conductor shall be transferred from one drum to another at the same time measuring its length with the help of a graduated pulley and Cyclometer. The difference in the average length thus obtained and as declared by the Bidder in the packing list shall be applied to all the drums if the conductor is found short during checking".

- SCHEDULE OF DEVIATIONS/VARIATIONS

If the tenderer has any exceptions to any of the clause/s laid down in this specification, these should beclearly stated in the schedule of deviations / variations.

SECTION - II  SPECIFIC TECHNICAL REQUIREMENTS

- SCOPE

This section of the specification covers climatic and isoceraunic conditions, specific technical particulars, schedule of requirements & desired deliveries, for conductor for 11/33 kV lines.

- CLIMATIC & ISOCERAUNIC CONDITIONS TO BE SPECIFIED BY EMPLOYER

  - 1Maximum Temperature

    - Conductor	ºC.

  - 2Minimum Temperature	ºC.

  - i)Max. ambient temperature	ºC

ii) Mean annual / every day temperature	ºC 2.4Basic wind speed m/s

  - Relative humidity

    - Maximum	%

    - Minimum	%

  - Average Rainfall (Max.) mm per annum

  - a)Rainy months	May to Sept.

15 Rainy days in a year (days)

  - Average number of thunder storm

  - Altitude varying from sea level

  - Basic horizontal Seismic Co-efficient(horizontal) Basic vertical Seismic Co-efficient

  - System Particulars

- Line Voltage (kV)

- Highest System Voltage (kV)

- Number of Circuits

- Frequency HZ

- Neutral

- Short circuit level (KA)

- SPECIFIC TECHNICAL REQUIREMENTS

| - Conductor: | ACSR Squirrel /Rabbit/Raccoon/Dog/Weasel/Panther |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| - IS applicable: | IS-398 (part-II) 1996 latest revision |  |  |  |  |  |
| 3. Wire Diameter | Squirrel | Rabbit | Raccoon | Dog | Weasel | Panther |
| Aluminium (mm) | 6/2.11 | 6/3.35 | 6/4.09 | 6/4.72 | 6/2.59 | 30/3.00 |
| Steel(mm) | 1/2.11 | 1/3.35 | 1/4.09 | 7/1.57 | 1/2.59 | 7/3.00 |
| 4. Number of strands: |  |  |  |  |  |  |
| Steel center | 1 | 1 | 1 | 1 | 1 | 1 |
| 1st steel layer |  | - |  | 6 |  | 6 |
| 1st Aluminium layer | 6 | 6 | 6 | 6 | 6 | 12 |
| 2nd Aluminium layer |  |  |  |  |  | 18 |
| 5. Sectional Area of Aluminium (sq. mm.) | 20.98 | 52.88 | 78.83 | 105 | 31.61 | 212.1 |
| 6. Total Sectional Area(sq.mm.) | 24.48 | 61.7 | 91.97 | 118.5 | 36.88 | 261.5 |
| 7. Overall diameter(mm) | 6.33 | 10.05 | 12.27 | 14.15 | 7.77 | 21 |
| 8. Approximate weight(Kg./Km.) | 85 | 214 | 319 | 394 | 128 | 974 |
| 9. Calculated D.C resistance at 20 degrees C., maximum. (Ohms/Km) | 1.394 | 0.5524 | 0.3712 | 0.2792 | 0.9289 | 0.139 |
| 10. Ultimate tensile strength (KN) | 7.61 | 18.25 | 26.91 | 32.41 | 11.12 | 89.67 |
| 11. Final modulus of elasticity (GN/sq.mtr) | 79 | 79 | 79 | 75 | 79 | 80 |
| 12. Coefficient of linear expansion x 10-6 per deg-C | 19.1 | 19.1 | 19.1 | 19.8 | 19.1 | 17.8 |
| 13. Lay ratio | Max/ Min | Max/ Min | Max/ Min | Max/ Min | Max/ Min | Max/ Min |
| Steel core 6 wire layer |  |  |  | 28/13 |  | 28/13 |
| Aluminium Ist layer | 14/10 | 14/10 | 14/10 | 14/10 | 14/10 | 14/10 |
| Aluminium 2nd layer |  |  |  |  |  | 16/10 |

14. Technical Particulars

| - Diameter-mm | Squirrel |  | Rabbit |  | Raccon |  | Dog |  | Weasel |  | Panther |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Al | Steel | Al | Steel | Al | Steel | Al | Steel | Al | Steel | Al | Steel |
| Standard(mm) IS: 398 /2; Table 3 | 2.11 | 2.11 | 3.35 | 3.35 | 4.09 | 4.09 | 4.72 | 1.57 | 2.59 | 2.59 | 3.00 | 3.00 |
| Maximum (mm) IS: 398 /2; Table 1 & Table 2 | 2.13 | 2.15 | 3.38 | 3.42 | 4.13 | 4.17 | 4.77 | 1.60 | 2.62 | 2.64 | 3.03 | 3.06 |
| Minimum (mm) IS: 398 /2; Table 1 & Table 2 | 2.09 | 2.07 | 3.32 | 3.28 | 4.05 | 4.01 | 4.67 | 1.54 | 2.56 | 2.54 | 2.97 | 2.94 |
| b. Cross-sectional area of nominal diameter wire (mm2) IS: 398 /2; Table 1 & Table 2 | 3.497 | 3.497 | 8.814 | 8.814 | 13.14 | 13.14 | 17.50 | 1.936 | 5.269 | 5.269 | 7.069 | 7.069 |
| - Weight (Kg./Km) IS: 398 /2; Table 1 & Table 2 | 9.45 | 27.27 | 23.82 | 68.75 | 35.51 | 102.48 | 47.30 | 15.10 | 14.24 | 41.09 | 19.11 | 55.13 |
| - Min. breaking load (KN) Before stranding | 0.63 | 4.60 | 1.43 | 11.58 | 2.08 | 17.27 | 2.78 | 2.70 | 0.89 | 6.92 | 1.17 | 9.29 |
| - Min. breaking load (KN) After stranding | 0.64 | 4.37 | 1.36 | 11.00 | 1.98 | 16.4 | 2.64 | 2.57 | 0.85 | 6.57 | 1.11 | 8.83 |
| - D.C resistance at 20̊C min. (Ohm/Km) | 8.237 |  | 3.265 |  | 2.194 |  | 1.650 |  | 5.490 |  | 4.079 |  |

- Zinc coating of steel core:

  - The steel strands shall be hot dip galvanized as per IS: 4826

  - Process of Galvanizing: Hot dip.

  - Quality of Zinc : IS-209/1979 or latest edition.

- Joints in strands

  - Steel : Not permitted

  - Aluminium: No joint shall be permitted in the Aluminum wires in the outer most layer of the ACSR conductor. But permitted in the inner layers such that no two such joints are within 15 meters of each other in the complete stranded conductor.

15.	Chemical composition of high carbon steel wire:

| Element | % Composition |
| --- | --- |
| i) Carbon | 0.5 to 0.85 |
| ii) Manganese | 0.5 to 1.10 |
| iii) Phosphorus | Not more than 0.035 |
| iv) Sulphur | Not more than 0.045 |
| v) Silicon | 0.10 to 0.35 |

AAA CONDUCTOR

  - TECHNICAL DESCRIPTION OF AAAC CONDUCTOR

  - DETAILS OF CONDUCTORS

    - The AAAC Conductors shall generally conform to IS: 398 (Part-IV), IEC:104-1987 except where otherwise specified herein.

    - The details of the AAAC Conductors of various sizes are given in the enclosed Table-I

  - WORKMANSHIP

    - All the Al-alloy strands shall be smooth, uniform and free from all imperfections, such as spills and splits, die marks, scratches, abrasions, etc., after drawing and also after stranding.

    - The finished conductor shall be smooth, compact, uniform and free from all imperfections including kinks (protrusion of wires), scuff marks, dents, pressmarks, cut marks, wire cross over, over riding, looseness (wire being dislocated by finger/hand pressure and/or unusual bangle noise on tapping), material inclusions, white rust, powder formation or black spot (on account of reaction with trapped rain water etc.), dirt, grit etc.

  - JOINTS IN WIRES

    - 1No joint shall be permitted in any layer of finished conductor.

  - STRANDING

In all constructions, the successive layers shall be stranded in opposite directions. The wires in each layer shall be evenly and closely stranded round the underlying wire or wires. The outer most layer of wires shall have a right hand lay. The lay ratio shall be as follow.

| Number of wires in conductor | 3/6 Wire layer |  | 12 Wire layer |  | 18 Wire layer |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Min | Max | Min | Max | Min | Max |
| 3 | 10 | 14 | - | - | - | - |
| 7 | 10 | 14 | - | - | - | - |
| 19 | 10 | 16 | 10 | 14 | - | - |
| 37 | 10 | 17 | 10 | 16 | 10 | 14 |

  - TOLERANCES

The manufacturing tolerances in diameter of individual aluminium alloy strand shall be as per Table-I.

  - MATERIALS

    - ALUMINUM ALLOY

The wire shall be of heat treated aluminum, magnesium silicon alloy having a composition appropriate to the mechanical & electrical properties as specified in IS 398(Part-4).

The Aluminum  Alloy strands drawn from heat treated aluminium alloy  redraw  rods  conforming  to  Type  B  as  per  IEC:104-latest

| amendment. The chemical composition conform to IS 1997-91, as given below: | of redrawn | rods | shall |
| --- | --- | --- | --- |
| Elements Si | Percent 0.50-0.90 |  |  |
| Mg | 0.60-0.90 |  |  |
| Fe | 0.50 max |  |  |
| Cu | 0.10 max |  |  |
| Mn | 0.03 max |  |  |
| Cr | 0.03 max |  |  |
| Zn | 0.10 max |  |  |
| B | 0.06 max |  |  |
| Other Element (Each) | 0.03 max |  |  |
| Other Element (Total) | 0.10 max |  |  |
| Al | Remainder |  |  |

  - STANDARD LENGTH

    - The standard length of the conductor shall be 2000 meters. A tolerance of +/-5% on the standard length offered by the Bidder shall  be permitted. All lengths outside this limit of tolerance shall be treated as random lengths. The conductor drums shall be adequate to wind one or more standard length of 2000 meters of SQUIRREL/WEASEL/RABIT/RACOON/DOG/ PANTHER AAA conductor.

    - Random lengths will be accepted provided no length is less than 70% of the standard length and the total quantity of such random lengths shall not be more than 10% of the total quantity ordered.

    - Bidder shall also indicate the maximum single length, above the standard length, he can manufacture in the guaranteed technical particulars of offer. The Owner reserves the right to place orders for the above lengths on the same terms and conditions applicable for the standard lengths during the execution of the Contract.

  - TESTS AND STANDARDS

The  following  tests  to  be  conducted  for  AAAC  conductors  shall conform to IS 398(Part -IV) 1979 and IEC 888 & 889.

    - TYPE/PERIODIC

The following tests shall be conducted on samples of each type of conductor :

| (a) | UTS test on stranded | ) |
| --- | --- | --- |
|  | conductor | ) |
|  |  | ) Annexure-A |
| (b) | DC resistance test on | ) |
|  | stranded conductor | ) |

    - ACCEPTANCE TESTS

| (a) | Visual check for joints scratches | ) Annexure - A |
| --- | --- | --- |
|  | etc. and length measurement of | ) |

conductor by rewinding	)

      - Dimensional check on	)

Al-alloy strands

      - Check for lay-ratio	)

)

      - Elongation test	)	Annexure - A

)

      - Breaking load/tensile  test on	) Aluminum alloy strands	)

)

      - DC resistance test on ) Aluminum alloy  strands)

      - Wrap test on  )	IEC 104, IEC 1089 Aluminum alloy  strands

| (h) | Visual and dimensional | ) |
| --- | --- | --- |
|  | check on drum | ) IS:1778-1980 |

    - ROUTINE TEST

- Check to ensure that there are no joints.

- Check that there are no cuts, fins etc. on the strands.

- Check that drums are as per Specification.

- All acceptance test as mentioned above to be carried out on each coil.

    - TESTS DURING MANUFACTURE

(a)	Chemical analysis of  )

Aluminum alloy  used for	)

making strands	)	Annexure-A

    - TESTING EXPENSES

- The type test charges for the conductor should be quoted in the relevant schedule of Bid Proposal Sheets.

- Contractor shall indicate the laboratories in which they propose to conduct the type tests. They shall ensure that adequate facilities are available in the laboratories and the tests can be completed in these laboratories within the time schedule guaranteed by them.

- In case of failure in any type test, the Contractor is either required to manufacture fresh sample lot and repeat all the tests successfully once or repeat that particular type test three times successfully on the sample selected from the already manufactured lot at his own expenses. In case a fresh lot is manufactured for testing, then the lot already manufactured shall be rejected.

- The entire cost of testing for the acceptance and routine tests and Tests during manufacture specified herein shall be treated as included in the quoted unit price of conductor, except for the expenses of the inspector/Owner's representative.

- In case of failure in any type test, if repeat type tests are required to be conducted, then all the expenses for deputation of Inspector/Owner's representative shall be deducted from  the contract price. Also if on receipt of the Contractor's notice  of testing, the Owner's representative does not find 'The material or testing facilities' to be ready for testing the expenses incurred by the Owner for re-deputation shall be deducted from contract price.

    - ADDITIONAL TESTS

- The Owner reserves the right of having at his own expenses any

other  test(s)  of  reasonable  nature  carried  out  at  Contractor’s

premises, at site or in any other place in addition to the aforesaid type, acceptance and routine tests to satisfy himself that the materials comply with the Specifications.

- The Owner also reserves the right to conduct all the tests mentioned in this specification at his own expense on the samples drawn from the site at Contractor’s premises or at any other test centre. In case of evidence of non-compliance, it shall be binding on the part of Contractor to prove the compliance of the items to the technical specifications by repeat tests, or correction of deficiencies, or replacement of defective items all without any extra cost to the Owner.

    - SAMPLE BATCH FOR TYPE TESTING

- The Contractor shall offer material for selection of samples for type testing only after getting Quality Assurance Plan approved from Owner’s Quality Assurance Deptt. The sample shall be manufactured strictly in accordance with the Quality Assurance Plan approved by Owner.

- The Contractor  shall offer at least three drums for selection of sample required for conducting all the type tests.

- The Contractor is required to carry out all the acceptance tests successfully in presence of Owner’s representative before sample selection.

    - TEST REPORTS

- Copies of type test reports shall be furnished in at least six copies along with one original. One copy will be returned duly certified by the Owner only after which the commercial production of the material shall start.

- Record of routine test reports shall be maintained by the Supplier at his works for periodic inspection by the Owner’s representative.

- Test Certificates of tests during manufacture shall be maintained by the Contractor. These shall be produced for verification as and when desired by the Owner.

  - INSPECTION

    - The Owner’s representative shall at all times be entitled to have access to the works and all places of manufacture, where conductor shall be manufactured and representative shall have full facilities for unrestricted inspection of the Contractor’s works, raw materials and process of manufacture for conducting necessary tests as detailed herein.

    - The Contractor shall keep the Owner informed in advance of the time of starting and of the progress of manufacture of conductor in its various stages so that arrangements can be made for inspection.

    - No material shall be dispatched from its point of manufacture before it has been satisfactorily inspected and tested, unless the inspection is waived off by the Owner in writing. In the latter case also, the conductor shall be dispatched only after satisfactory testing for all tests specified herein have been completed.

    - The acceptance of any quantity of material shall in no way relieve the Contractor of any of his responsibilities for meeting all requirements of the Specification, and shall not prevent subsequent rejection if such material is later found to be defective.

    - TEST FACILITIES

The  following  additional  test  facilities  shall  be  available  at  the

Contractor’s works:

- Calibration of various testing and measuring equipment including tensile testing machine, resistance measurement facilities, burette, thermometer, barometer etc.

- Standard resistance for calibration of resistance bridges.

- Finished conductor shall be checked for length verification and surface finish on separate rewinding machine at reduced speed (variable from 8 to 16 meters per minute). The rewinding facilities shall have appropriate clutch system and free of vibrations, jerks etc. with traverse laying facilities.

  - PACKING

    - The conductor shall be supplied in non-returnable, strong, wooden drums provided with lagging of adequate strength, constructed to protect the conductor against any damage and displacement during transit, storage and subsequent handling and stringing operations in the field. The Contractor shall be responsible for any loss or damage during transportation handling and storage due to improper packing. The drums shall generally conform to IS:1778-1980, except as otherwise specified hereinafter.

    - The drums shall be suitable for wheel mounting and for letting off the conductor under a minimum controlled tension of the order of 5 KN.

    - The Contractor should submit their proposed drum drawings along with the bid.

    - The Contractor may offer more than one length of the conductor in a single drum.

    - All wooden components shall be manufactured out of seasoned soft wood free from defects that may materially weaken the component parts of the drums. Preservative treatment  shall  be  applied  to  the  entire  drum  with

preservatives  of  a  quality,  which  is  not  harmful  to  the conductor.

    - The flanges shall be of two ply construction with a total thickness of 64 mm with each ply at right angles to the adjacent ply and nailed together. The nails shall be driven from the inside face flange, punched and then clenched on the outer face. Flange boards shall not be less than the nominal thickness by more than 2mm. There shall not be less than 2 nails per board in each circle. Where a slot is cut in the flange to receive the inner end of the conductor the entrance shall be in line with the periphery of the barrel.

    - The wooden battens used for making the barrel of the conductor shall be of segmental type. These shall be nailed to the barrel supports with at least two nails. The battens shall be closely butted and shall provide a round barrel with smooth external surface. The edges of the battens shall be rounded or chamfered to avoid damage to the conductor.

    - Barrel studs shall be used for the construction of drums. The flanges shall be holed and the barrel supports slotted to receive them. The barrel studs shall be threaded over a length on either end, sufficient to accommodate washers, spindle plates and nuts for fixing flanges at the required spacing.

    - Normally, the nuts on the studs shall stand protruded of the flanges. All the nails used on the inner surface of the flanges and the drum barrel shall be counter sunk. The ends of barrel shall generally be flushed with the top of the nuts.

    - The inner cheek of the flanges and drum barrel surface shall be painted with a bitumen based paint.

    - Before reeling, card board or double corrugated or thick bituminous water-proof bamboo paper or HDPE sheet shall be secured to the drum barrel and inside of flanges of the drum by means of  a  suitable  commercial  adhesive  material.    The  paper should be dried before use. After reeling the conductor the exposed surface of the outer layer of conductor shall be wrapped with thin polythene sheet across the flanges to preserve the conductor from dirt, grit and damage during transportation and handling and also to prevent ingress of rain water during storage/transport.

    - A minimum space of 75 mm for conductor shall be provided between the inner surface of the external protective lagging and outer layer of the conductor. Outside the protective lagging, there shall be minimum of two binders consisting of hoop iron/ galvanized steel wire. Each protective lagging shall have two recesses to accommodate the binders.

    - Each batten shall be securely nailed across grains as far as possible to the flange, edges with at least 2 nails per end. The length of the nails shall not be less than twice the thickness of the battens. The nails shall not protrude above the general surface and shall not have exposed sharp, edges or allow the battens to be released due to corrosion.

    - The nuts on the barrel studs shall be tack welded on the one side in order to fully secure them. On the second end, a spring washer shall be used.

    - A steel collar shall be used to secure all barrel studs. This collar shall be located between the washers and the steal drum and secured to the central steel plate by welding.

    - Outside the protective lagging, there shall be minimum of two binder consisting of hoop iron/ galvanized steel wire. Each protective lagging shall have two recesses to accommodate the binders.

    - The conductor ends shall be properly sealed and secured with the help of U-nail on the side of one of the flanges to avoid loosening of the conductor layers during transit and handling.

    - As an alternative to wooden drum Contractor may also supply the conductors in returnable painted steel drums. After preparation of steel surface according to IS : 9954, synthetic enamel paint shall be applied after application of one coat of primer. Wooden/Steel drum will be treated at par for evaluation purpose and accordingly the Contractor should quote in the package.

  - MARKING

Each drum shall have the following information stenciled on it in indelible ink along with other essential data :

- Contract/Award letter number.

- Name and address of consignee.

- Manufacturer’s name and address.

- Drum and lot number

- Size and type of conductor

- Length of conductor in meters

- Arrow marking for unwinding

- Position of the conductor ends

- Number of turns in the outer most layer.

- Gross weight of drum after putting lagging.

- Average weight of the drum without lagging.

- Net weight of the conductor in the drum.

- Month and year of manufacture of conductor

The above should be indicated in the packing list also.

  - VERIFICATION OF CONDUCTOR LENGTH

The Owner reserves the right to verity the length of conductor after unreeling at least Two (2) percent of the drums in a lot offered for inspection.

For the balance drums, length verification shall be done by the owner based on report/certification from Manufacturer/Contractor.

  - STANDARDS

    - The conductor shall conform to the  following Indian/International Standards, which shall mean latest revisions, with amendments/changes adopted  and published, unless specifically stated otherwise in  the Specification.

    - In the event of the supply of conductor conforming to standards other than specified, the Bidder shall confirm in his bid that these standards are equivalent to those specified. In case of award, salient features of comparison between the standards proposed by the Contractor and those specified in this document will be provided by the Contractor to establish their equivalence.

––––––———————————————————————————

Sl.	Indian	Title International

No.	Standard	Standards

——————————————————————————————

| 1. | IS:398 (Part-IV) | Aluminum Alloy | IEC : 208-1966 |
| --- | --- | --- | --- |
|  |  | stranded conductor | BS-3242-1970 |

2	IS : 9997-1988 Aluminum Alloy	IEC 104-1987

Redraw Rods

3	IS : 1778-1980 Reels and Drums	BS:1559-1949

for Bare Conductors

——————————————————————————————

1.0	TESTS ON AAAC CONDUCTORS

1.1	UTS Test on Stranded Conductor

ANNEXURE-A

Circles perpendicular to the axis of the conductor shall be marked at two places on a sample of conductor of minimum 5 m length between fixing arrangement suitably fixed on a tensile testing machine. The load shall be increased at a steady rate upto 50% of minimum specified UTS and held for one minute. The circles drawn shall not be distorted due to relative movement of strands. Thereafter the load shall be increased at steady rate to minimum UTS and held for one minute. The Conductor sample shall not fail during this period. The applied load shall then be increased until the failing load is reached and the value recorded.

  - D.C. Resistance Test on Stranded Conductor

On a conductor sample of minimum 5m length two contact-clamps shall be fixed with a predetermined bolt torque. The resistance shall be measured by a Kelvin double bridge by placing the clamps initially zero meter and subsequently one meter apart. The test shall be repeated at least five times and the average value recorded. The value obtained shall be corrected to the value at 20°C as per IS:398- (Part-V)-1982. The resistance corrected at 200C shall conform to the requirements of this Specification.

  - CHEMICAL ANALYSIS OF ALUMINIUM ALLOY

Samples taken from the Aluminium alloy ingots/coils/strands shall be chemically/spectrographically analyzed. The same shall be in conformity to the requirements stated in this Specification.

  - VISUAL AND DIMENSIONAL CHECK ON DRUMS

The drums shall be visually and dimensionally checked to ensure that they conform to the requirements of this Specification.

  - VISUAL CHECK FOR JOINTS, SCRATCHES ETC.

Conductor drums shall be rewound in the presence of the Owner. The Owner shall visually check for scratches, joints etc. and that the conductor generally conforms to the requirements of this Specification. Two percent (2%) drums from each lot shall be rewound in the presence of the Owner's representative.

  - DIMENSIONAL CHECK ON ALUMINUM ALLOY STRANDS

The individual strands shall be dimensionally checked to ensure that they conform to the requirement of this Specification.

1.7	CHECK FOR LAY-RATIOS OF VARIOUS LAYERS

The lay-ratios of various layers shall be checked to ensure that they conform to the requirements of this Specification.

  - TORSION AND ELONGATION TESTS ON ALUMINUM ALLOY STRANDS

The test procedures shall be as per clause No. 10.3 of IEC : 888. In torsion test, the number of complete twists before fracture shall not be less than 18 on a length equal to 100 times the standard diameter of the strand. In case test sample length is less or more than 100 times the stranded diameter of the strand, the minimum number of twists will be proportioned to the length and if number comes in the fraction then it will be rounded off to next higher whole number. In elongation test, the elongation of the strand shall not be less than 4% for a gauge length of 250 mm.

  - CHECK ON BARREL BATTEN STRENGTH OF DRUMS

The details regarding barrel batten strength test will be discussed and mutually agreed to by the Contractor & Owner in the Quality Assurance Programme.

  - Breaking Load Test on Individual Aluminium Alloy Wires

The test shall be conducted  on  Aluminum  alloy  wires. The breaking load of one specimen cut from each of the samples taken shall be determined by means of suitable tensile testing machine. The load shall be applied gradually Si the jaws of the testing machine shall be not less than 25 mm/min. and not greater than 100 mm./ min. The ultimate breaking load of the specimens shall be not less than the values specified in the Specification.

  - RESISTANCE TEST ON ALUMINUM ALLOY WIRE

The test shall be conducted on aluminium alloy wires only, conforming to procedure as per IEC: 889. The electrical resistance of one specimen of aluminium wire cut from each of the samples taken shall be measured at ambient temperature. The  measured  resistance  shall  be  corrected  to  the value corresponding to 20 degree C. by means of following formula.

1

R20	=	RT -------------------

1+alpha x (T-20)

Where

R20	=	Resistance corrected at 20 degrees C.

RT	=	Resistance measured at T degrees C.

alpha =	Constant	mass	temperature	coefficient	of resistance 0.004.

T	=	Ambient temperature during measurement

This resistance calculated to 20 degrees C. shall be not more than the maximum value specified in the specification.

Table-1

Details of parameters of AAA conductor

| S.N . | Parameter | Squirrel | Weasel | Rabbit | Raccon | Dog | Wolf | Panther |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1 | Total sectional area of conductor (sqmm) | 22 | 34 | 55 | 80 | 100 | 173 | 232 |
| 2 | (No of Al strand/dia in mm) | 7/2.00 | 7/2.50 | 7/3.15 | 7/3.81 | 7/4.26 | 19/3.40 | 19/3.94 |
| 3 | Overall diameter (mm) | 6 | 7.5 | 9.45 | 11.43 | 12.78 | 17 | 19.7 |
| 4 | approx mass (kg/km) | 60.16 | 94 | 149.2 | 218.26 | 272.86 | 474.02 | 636.67 |
| 5 | Resistance at 20 deg cel (ohms/km) | 1.541 | 0.99 | 0.621 | 0.425 | 0.339 | 0.1969 | 0.1471 |
| 6 | approx calculated breaking load (kN) | 6.45 | 10.11 | 16.03 | 23.41 | 29.26 | 50.54 | 68.05 |
| 7 | Final modulus of Elasticity (kg/sq cm) | 0.6324 x 106 | 0.6324 x 106 | 0.6324 x 106 | 0.6324 x 106 | 0.6324 x 106 | 0.612 x106 | 0.612x 106 |
| 8 | Coefficient of linear Expansion /˚C | 23.0 x 10-6 | 23.0 x 10-6 | 23.0 x 10-6 | 23.0 x 10-6 | 23.0 x 10-6 | 23.0 x 10-6 | 23.0 x 10-6 |

| S.N . | Parameter | Squirrel | Weasel |  | Rabbit | Raccon | DOG | wolf | Panther |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 9. Details of Aluminium Strands |  |  |  |  |  |  |  |  |  |
| a | Minimum breaking load of the strand before stranding (kN) | 0.97 | 1.52 | 2.41 |  | 3.52 | 4.4 | 2.8 | 3.77 |
| b | Minimum breaking load of the strand after stranding (kN) | 0.92 | 1.44 | 2.29 |  | 3.34 | 4.18 | 2.66 | 3.58 |
| c | Maximum DC resistance of strands at 20 deg C (ohms/km) | 10.653 | 6.845 | 4.29 |  | 2.938 | 2.345 | 3.677 | 2.746 |
| d | Mass (kg/km) | 8.482 | 13.25 | 21.04 |  | 30.78 | 30.48 | 24.51 | 32.92 |
| e | Diameter |  |  |  |  |  |  |  |  |
| i | Nominal | 2.0 | 2.50 | 3.15 |  | 3.81 | 4.26 | 3.40 | 3.94 |
| ii | Maximum | 2.02 | 2.53 | 3.18 |  | 3.85 | 4.30 | 3.43 | 3.98 |
| iii | Minimum | 1.98 | 2.47 | 3.12 |  | 3.77 | 4.22 | 3.37 | 3.90 |

Table-1 (Contd…)

Details of parameters of AAA conductor